## Cover
Client: |  | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
Cover
CUSTOMER: |  | ALINVEST | PREPARED: | JOBI
PROJECT CODE: |  | E2558 | REVIEWED: | ANSA
PROJECT NAME: |  | ALFAGEN | DATE: | 2025/12/04
CONTRACTOR DOC. CODE: |  | 2558-3311-HGS-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: |  | 2558-3311-HGS-E-LST-CBLS | PAGE: | 01 of 04
REVISION CONTROL
REV | DATE | DESCRIPTON |  | PAGE
A | 2025/12/04 | Issue for information |  | 1-4
B
C
D
E
F
G
H
I
J
K
L
M
N
O
P
Q
R
S
T
U
V
W
X
Y
Z
AA
AB
AC
AD
AE
The drawing(s), document(s) and the information contained herein are the property of INDUSTRIAL FURNACES INSERTEC. And they shall not be disclosed, reproduced or used in any manner without the prior written consent of INDUSTRIAL FURNACES INSERTEC. Offenders will be held liable for the payment of damages.

## Table of Contents
Client: |  | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
Table of contents
CUSTOMER: |  | ALINVEST | PREPARED: | JOBI
PROJECT CODE: |  | E2558 | REVIEWED: | ANSA
PROJECT NAME: |  | ALFAGEN | DATE: | 2025/12/04
CONTRACTOR DOC. CODE: |  | 2558-3311-HGS-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: |  | 2558-3311-HGS-E-LST-CBLS | PAGE: | 02 of 04
Table of contents
SEC | DESCRIPTON |  |  | PAGE
0 | Cover |  |  | 1-7
1 | Table of contents |  |  | 2
2 | Definitions |  |  | 3
3 | Equipment cable list |  |  | 4
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
The drawing(s), document(s) and the information contained herein are the property of INDUSTRIAL FURNACES INSERTEC. And they shall not be disclosed, reproduced or used in any manner without the prior written consent of INDUSTRIAL FURNACES INSERTEC. Offenders will be held liable for the payment of damages.

## Definitions
Client: | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
DEFINITIONS
CUSTOMER: | ALINVEST | PREPARED: | JOBI
PROJECT CODE: | E2558 | REVIEWED: | ANSA
PROJECT NAME: | ALFAGEN | DATE: | 2025/12/04
CONTRACTOR DOC. CODE: | 2558-3311-HGS-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: | 2558-3311-HGS-E-LST-CBLS | PAGE: | 03 of 04
MAIN DEFINITIONS
== -
= -
++ -
+ -
Description -
IME (Complete) -
Tag - For more detail, please refer to B001-B002-GEN-E-PRC-NPOS-R09 Numbering procedure for electrical objects and signals document.
Category - For more detail, please refer to B001-B002-GNL-E-SPC-INCC-R02 Technical specification for cables and cable trays document.
Type - Cable type according to conductor number, section, shield, etc
Length - Estimated lenght of the given cable.
Page - Page number realted to the electrical schematics. Refer to: B001-B002-B003-E-DWG-ESCH-R00 Equipment electrical schematics
Function -
Remarks - Notes to be considered.
Revision change comments - Revision change reason comments.

## Equipment cable list
Client: | CUSTOMER: | ALINVEST |  | EQUIPMENT CABLE LIST | [7 empty] | PREPARED: | JOBI | Contractor:
ALINVEST | PROJECT CODE: | E2558 | [9 empty] | REVIEWED: | ANSA
| PROJECT NAME: | ALFAGEN | [9 empty] | DATE: | 2025/12/04
| CONTRACTOR DOC. CODE: | 2558-3311-HGS-E-LST-CBLS | [9 empty] | REVISION: | A
| CUSTOMER DOC. CODE: | 2558-3311-HGS-E-LST-CBLS | [9 empty] | PAGE: | 04 of 04
SOURCE |  |  | CABLE | [5 empty] | DESTINATION |  |  | OTHERS
Location Description | Instrument Description | Device Tag | Tag | Category | Type | Length [m] | Cable Reference | Route | Device Tag | Instrument Description | Location Description | Scope of Supply | Remarks | Revision Change Comment
T141.62 | - | r41.62 | WL41.62 | CWP01 | 4G35 | TBD BY CLIENT | - | - | r41.62-3311-HGS-GEN01-PCP01 | - | Billet Cast MCC Room | AIB | - | -
T141.62 | - | r41.62 | WL41.62.L1 | CWP01 | 3G2,5 | TBD BY CLIENT | - | - | r41.62-3311-HGS-GEN01-PCP01 | - | Billet Cast MCC Room | AIB | - | -
Billet Cast MCC Room | - | r41.31-0311-GEN-APU01-PDP01 | r41.31-0311-GEN-APU01-PDP01-WP06 | CWP01 | 3G2,5 | 15 | RV-K 0,6/1kV | - | r41.62-3311-HGS-GEN01-PCP01 | - | Billet Cast MCC Room | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WP01 | CWP01 | 4G25 | 75 | RV-K 0,6/1kV | - | r41.62-3311-HGS-GEN01-DSS01 | - | PMS 400V busbar disconnector switch box Zone#01 | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WP02 | CWP01 | 4G25 | 70 | RV-K 0,6/1kV | - | r41.62-3311-HGS-GEN01-DSS02 | - | PMS 400V busbar disconnector switch box MAI Zone | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC01 | CWC01 | 7G1,5 | 75 | YSLY 300/500V | - | r41.62-3311-HGS-GEN01-LCB01 | - | Zone#01 400Vac energy indicator local control Box | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC02 | CWC01 | 7G1,5 | 70 | YSLY 300/500V | - | r41.62-3311-HGS-GEN01-LCB02 | - | MAI 400Vac energy indicator local control Box | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WP03 | CWP01 | 3G4 | 75 | RV-K 0,6/1kV | - | r41.62-3311-HGS-GEN01-DSS03 | - | PMS 230V-UPS busbar disconnector switch box Zone#01 | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WP04 | CWP01 | 3G4 | 70 | RV-K 0,6/1kV | - | r41.62-3311-HGS-GEN01-DSS04 | - | PMS 230V-UPS busbar disconnector switch box MAI Zone | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC03 | CWC01 | 7G1,5 | 75 | YSLY 300/500V | - | r41.62-3311-HGS-GEN01-LCB03 | - | MAI 230Vac-UPS energy indicator local control Box | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC04 | CWC01 | 7G1,5 | 70 | YSLY 300/500V | - | r41.62-3311-HGS-GEN01-LCB04 | - | Zone#01 230Vac-UPS energy indicator local control Box | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WP05 | CWP01 | 3G2,5 | 70 | RV-K 0,6/1kV | - | r41.62-3311-HGS-GEN01-CJB01 | - | Communication data rail | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC05 | CWC01 | 4G1,5 | 70 | YSLY 300/500V | - | r41.62-3311-HGS-GEN01-CJB01 | - | Communication data rail | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WE02 | CWE02 | SF/UTP | 70 | 6XV1870-2B | - | r41.62-3311-HGS-GEN01-CJB01 | - | Data rail communication junction box | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC10 | CWC01 | 7G1,5 | 50 | YSLY 300/500V | - | r41.62-3311-HGS-GEN01-LCB05 | - | Technical room access local control box | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC11 | CWC01 | 3G1,5 | 50 | YSLY 300/500V | - | 3311-HGS-GEN01-ACC01-XRA3101 | Billet area technical room safety registry access | - | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC12 | CWC01 | 5G1,5 | 50 | YSLY 300/500V | - | 3311-HGS-GEN01-ACC01-XRA3101 | Billet area technical room safety registry access | - | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC13 | CWC01 | 7G1,5 | 50 | YSLY 300/500V | - | r41.62-3311-HGS-GEN01-LCB06 | - | Main corridor access local control box | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC14 | CWC01 | 3G1,5 | 50 | YSLY 300/500V | - | 3311-HGS-GEN01-ACC02-XRA3101 | HGS corridor main safety registry access | - | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC15 | CWC01 | 5G1,5 | 50 | YSLY 300/500V | - | 3311-HGS-GEN01-ACC02-XRA3101 | HGS corridor main safety registry access | - | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC16 | CWC01 | 7G1,5 | 70 | YSLY 300/500V | - | r41.62-3311-HGS-GEN01-LCB07 | - | Maintenance corridor access local control box | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC17 | CWC01 | 3G1,5 | 70 | YSLY 300/500V | - | 3311-HGS-GEN01-ACC03-XRA3101 | HGS corridor maintenance safety registry access | - | AIB | - | -
Billet Cast MCC Room | - | r41.62-3311-HGS-GEN01-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC12 | CWC01 | 5G1,5 | 70 | YSLY 300/500V | - | 3311-HGS-GEN01-ACC03-XRA3101 | HGS corridor maintenance safety registry access | - | AIB | - | -
PMS 400V busbar disconnector switch box Zone#01 | - | r41.62-3311-HGS-GEN01-DSS01 | r41.62-3311-HGS-GEN01-DSS01-WP01 | CWP01 | 4G25 | 3 | RV-K 0,6/1kV | - | r41.62-3311-HGS-GEN01-PDR01 | - | Power distribution rail | IFI | - | -
PMS 400V busbar disconnector switch box Zone#01 | - | r41.62-3311-HGS-GEN01-DSS03 | r41.62-3311-HGS-GEN01-DSS03-WP01 | CWP01 | 3G4 | 3 | RV-K 0,6/1kV | - | r41.62-3311-HGS-GEN01-PDR01 | - | Power distribution rail | IFI | - | -
Data rail communication junction box | - | r41.62-3311-HGS-GEN01-CJB01 | r41.62-3311-HGS-GEN01-CJB01-WE01 | CWE02 | SMGM-VL-3000-QLS-N-RG316D (3M) | 3 | SMGM-VL-3000-QLS-N-RG316D (3M) | - | r41.62-3311-HGS-GEN01-CDR01 | - | Communication data rail | IFI | - | -
PMS 400V busbar disconnector switch box MAI Zone | - | r41.62-3311-HGS-GEN01-DSS02 | r41.62-3311-HGS-GEN01-DSS02-WP01 | CWP01 | 4G25 | 3 | RV-K 0,6/1kV | - | r41.62-3311-HGS-GEN01-PDR02 | - | Power distribution rail | IFI | - | -
PMS 400V busbar disconnector switch box MAI Zone | - | r41.62-3311-HGS-GEN01-DSS04 | r41.62-3311-HGS-GEN01-DSS04-WP01 | CWP01 | 3G4 | 3 | RV-K 0,6/1kV | - | r41.62-3311-HGS-GEN01-PDR02 | - | Power distribution rail | IFI | - | -
Power distribution rail | - | r41.62-3311-HGS-GEN01-PDR0X | r41.62-3311-HGS-TRS01-PIO01-WP20 | CWP01 | 4G10 | 4 | RV-K 0,6/1kV | - | r41.62-3311-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI | - | -
Power distribution rail | - | r41.62-3311-HGS-GEN01-PDR0X | r41.62-3311-HGS-TRS01-PIO01-WP21 | CWP01 | 4G10 | 4 | RV-K 0,6/1kV | - | r41.62-3311-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI | - | -
Power distribution rail | - | r41.62-3311-HGS-GEN01-PDR0X | r41.62-3311-HGS-TRS01-PIO01-WP22 | CWP01 | 2X1,5 | 4 | RV-K 0,6/1kV | - | r41.62-3311-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI | - | -
Power distribution rail | - | r41.62-3311-HGS-GEN01-PDR0X | r41.62-3311-HGS-TRS01-PIO01-WP23 | CWP01 | 2X1,5 | 4 | RV-K 0,6/1kV | - | r41.62-3311-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI | - | -
Communication data rail | - | r41.62-3311-HGS-GEN01-CDR01 | r41.62-3311-HGS-TRS01-PIO01-WE01 | CWE02 | SMGM-VL-3000-QLS-N-RG316D (3M) | 3 | SMGM-VL-3000-QLS-N-RG316D (3M) | - | r41.62-3311-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WP01 | CWP01 | 4G10 | 4 | RV-K 0,6/1kV | - | 3311-HGS-PMS01-ROT01-M01 (VFPS03) | PMS Rotation motor | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WP02 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3311-HGS-ESR70-ACR01-M01A (D03) | Cooling fan motor #A | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WP03 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3311-HGS-ESR70-ACR01-M01B (D03) | Cooling fan motor #B | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WP04 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3311-HGS-TRS01-GEN01-M01 (VFPS04) | Platform Translation motor | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WP05 | CWP01 | 3G2,5 | 4 | RV-K 0,6/1kV | - | 3311-HGS-TRS01-GEN01-M01 (VFPS04) | Platform Translation motor | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WP06 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3311-HGS-ESR40-HYG01-M01 (D03) | Hydraulic group pump motor | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC01 | CWC03 | TC K | 4 | SIL-FV-MM | - | 3311-HGS-PMS01-GEN01-TE1001 | Rotation thermocouple | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC02 | CWC02 | 2x1+SH | 4 | RC4V-K 300/500V | - | 3311-HGS-ESR70-ACR01-TS0711 | Cooling fan motor winding temperature M1A | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC03 | CWC02 | 2x1+SH | 4 | RC4V-K 300/500V | - | 3311-HGS-ESR70-ACR01-TS0712 | Cooling fan motor winding temperature M1B | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC04 | CWC02 | 7G1+SH | 4 | RC4V-K 300/500V | - | 3311-HGS-TRS01-GEN01-ZE1203 | Translation encoder | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC05 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3311-HGS-TRS01-MVP01-ZS1214 | PMS up | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC06 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3311-HGS-TRS01-MVP01-ZS1215 | PMS down | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC28 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3311-HGS-TRS01-GEN01-LS1201 | Traslation Limit Switch Forward | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC29 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3311-HGS-TRS01-GEN01-LS1202 | Traslation Limit Switch Backward | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC07 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3311-HGS-ESR40-HYG01-SV0410A | Solenoid valve PMS UP | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC08 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3311-HGS-ESR40-HYG01-SV0401B | Solenoid valve PMS DOWN | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC09 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3311-HGS-ESR40-GEN01-SV0401A | Solenoid valve PMS up feedback | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC10 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3311-HGS-ESR40-GEN01-SV0401B | Solenoid valve PMS down feedback | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC22 | CWC02 | 3G1+SH | 4 | RC4V-K 300/500V | - | 3311-HGS-ESR40-HYG01-PT0409 | Oil Filter Pressure Trasmitter | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC12 | CWC02 | 3G1+SH | 4 | RC4V-K 300/500V | - | 3311-HGS-ESR40-HYG01-LT0403 | Oil level switch Low | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC14 | CWC02 | 3G1+SH | 4 | RC4V-K 300/500V | - | 3311-HGS-ESR40-HYG01-LT0405 | Oil temperature trasmitter | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC15 | CWC02 | 5G1+SH | 4 | RC4V-K 300/500V | - | 3311-HGS-ESR40-HYG01-TE0406 | Oil pressure trasmitter #1 | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC16 | CWC02 | 5G1+SH | 4 | RC4V-K 300/500V | - | 3311-HGS-ESR40-GEN01-PT0407 | Oil Pressure transmiter #2 | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC17 | CWC02 | 5G1+SH | 4 | RC4V-K 300/500V | - | 3311-HGS-ESR40-GEN01-PT0408 | Oil Pressure transmiter #3 | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC18 | CWC02 | 12G1+SH | 4 | RC4V-K 300/500V | - | 3311-HGS-TRS01-GEN01-ZE1204A | Front safety scanner | - | IFI | - | -
TRS Power IO panel | - | r41.62-3311-HGS-TRS01-PIO01 | r41.62-3311-HGS-TRS01-PIO01-WC19 | CWC02 | 12G1+SH | 4 | RC4V-K 300/500V | - | 3311-HGS-TRS01-GEN01-ZE1204B | Back safety scanner | - | IFI | - | -