## Cover
Client: |  | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
Cover
CUSTOMER: |  | ALINVEST | PREPARED: | JOBI
PROJECT CODE: |  | E2558 | REVIEWED: | ANSA
PROJECT NAME: |  | ALFAGEN | DATE: | 2025/12/02
CONTRACTOR DOC. CODE: |  | 2558-3321-HGS-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: |  | 2558-3321-HGS-E-LST-CBLS | PAGE: | 01 of 07
REVISION CONTROL
REV | DATE | DESCRIPTON |  | PAGE
A | 2025/12/02 | Issue for information |  | 1-7
B
C
D
E
F
G
H
I
J
K
L
M
N
O
P
Q
R
S
T
U
V
W
X
Y
Z
AA
AB
AC
AD
AE
The drawing(s), document(s) and the information contained herein are the property of INDUSTRIAL FURNACES INSERTEC. And they shall not be disclosed, reproduced or used in any manner without the prior written consent of INDUSTRIAL FURNACES INSERTEC. Offenders will be held liable for the payment of damages.

## Table of Contents
Client: |  | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
Table of contents
CUSTOMER: |  | ALINVEST | PREPARED: | JOBI
PROJECT CODE: |  | E2558 | REVIEWED: | ANSA
PROJECT NAME: |  | ALFAGEN | DATE: | 2025/12/02
CONTRACTOR DOC. CODE: |  | 2558-3321-HGS-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: |  | 2558-3321-HGS-E-LST-CBLS | PAGE: | 02 of 07
Table of contents
SEC | DESCRIPTON |  |  | PAGE
0 | Cover |  |  | 1-7
1 | Table of contents |  |  | 2
2 | Definitions |  |  | 3
3 | Equipment cable list |  |  | 4-7
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
The drawing(s), document(s) and the information contained herein are the property of INDUSTRIAL FURNACES INSERTEC. And they shall not be disclosed, reproduced or used in any manner without the prior written consent of INDUSTRIAL FURNACES INSERTEC. Offenders will be held liable for the payment of damages.

## Definitions
Client: | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
DEFINITIONS
CUSTOMER: | ALINVEST | PREPARED: | JOBI
PROJECT CODE: | E2558 | REVIEWED: | ANSA
PROJECT NAME: | ALFAGEN | DATE: | 2025/12/02
CONTRACTOR DOC. CODE: | 2558-3321-HGS-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: | 2558-3321-HGS-E-LST-CBLS | PAGE: | 03 of 07
MAIN DEFINITIONS
== -
= -
++ -
+ -
Description -
IME (Complete) -
Tag - For more detail, please refer to B001-B002-GEN-E-PRC-NPOS-R09 Numbering procedure for electrical objects and signals document.
Category - For more detail, please refer to B001-B002-GNL-E-SPC-INCC-R02 Technical specification for cables and cable trays document.
Type - Cable type according to conductor number, section, shield, etc
Length - Estimated lenght of the given cable.
Page - Page number realted to the electrical schematics. Refer to: B001-B002-B003-E-DWG-ESCH-R00 Equipment electrical schematics
Function -
Remarks - Notes to be considered.
Revision change comments - Revision change reason comments.

## Equipment cable list
Client: | CUSTOMER: | ALINVEST |  | EQUIPMENT CABLE LIST | [7 empty] | PREPARED: | JOBI | Contractor:
ALINVEST | PROJECT CODE: | E2558 | [9 empty] | REVIEWED: | ANSA
| PROJECT NAME: | ALFAGEN | [9 empty] | DATE: | 2025/12/02
| CONTRACTOR DOC. CODE: | 2558-3321-HGS-E-LST-CBLS | [9 empty] | REVISION: | A
| CUSTOMER DOC. CODE: | 2558-3321-HGS-E-LST-CBLS | [9 empty] | PAGE: | 04/07 of 07
SOURCE |  |  | CABLE | [5 empty] | DESTINATION |  |  | OTHERS
Location Description | Instrument Description | Device Tag | Tag | Category | Type | Length [m] | Cable Reference | Route | Device Tag | Instrument Description | Location Description | Scope of Supply | Remarks | Revision Change Comment
T143.62 | - | r43.62 | WL43.62.R1 | CWP01 | 1x240 | TBD BY CLIENT | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PCP01 | - | Strip cast electrical room #01 | AIB
T143.62 | - | r43.62 | WL43.62.S1 | CWP01 | 1x240 | TBD BY CLIENT | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PCP01 | - | Strip cast electrical room #01 | AIB
T143.62 | - | r43.62 | WL43.62.T1 | CWP01 | 1x240 | TBD BY CLIENT | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PCP01 | - | Strip cast electrical room #01 | AIB
T143.62 | - | r43.62 | WL43.62.P1 | CWP01 | 1x120 | TBD BY CLIENT | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PCP01 | - | Strip cast electrical room #01 | AIB
T143.62 | - | r43.62 | WL43.62.L1 | CWP01 | 3G2,5 | TBD BY CLIENT | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PCP01 | - | Strip cast electrical room #01 | AIB
Billet Cast MCC Room | - | r41.31-0311-GEN-APU01-PDP01 | r41.31-0311-GEN-APU01-PDP01-WP01 | CWP01 | 3G2,5 | 15 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PCP01 | - | Strip cast electrical room #01 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WP01 | CWP01 | 4G35 | 80 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-DSS01 | - | PMS 400V busbar disconnector switch box Zone#01 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WC01 | CWC01 | 7G1,5 | 80 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-DSS01 | - | PMS 400V busbar disconnector switch box Zone#01 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WP03 | CWP01 | 3G2,5 | 80 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-CJB01 | - | Data rail communication junction box | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WP04 | CWP01 | 4G25 | 112 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-DSS02 | - | PMS 400V busbar disconnector switch box Maintenance#01 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WC04 | CWC01 | 7G1,5 | 112 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-DSS02 | - | PMS 400V busbar disconnector switch box Maintenance#01 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WP06 | CWP01 | 4G25 | 112 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-DSS03 | - | PMS 400V busbar disconnector switch box Zone#02 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WC06 | CWC01 | 7G1,5 | 112 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-DSS03 | - | PMS 400V busbar disconnector switch box Zone#02 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WP08 | CWP01 | 4G25 | 138 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-DSS04 | - | PMS 400V busbar disconnector switch box Maintenance#02 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WC08 | CWC01 | 7G1,5 | 138 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-DSS04 | - | PMS 400V busbar disconnector switch box Maintenance#02 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WP10 | CWP01 | 4G25 | 140 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-DSS05 | - | PMS 400V busbar disconnector switch box Zone#03 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WC10 | CWC01 | 7G1,5 | 140 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-DSS05 | - | PMS 400V busbar disconnector switch box Zone#03 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WP02 | CWP01 | 3G4 | 80 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-DSS06 | - | PMS 230V busbar disconnector switch box Zone#01 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WC02 | CWC01 | 7G1,5 | 80 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-DSS06 | - | PMS 230V busbar disconnector switch box Zone#01 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WC03 | CWC01 | 4G1,5 | 80 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-CJB01 | - | Data rail communication junction box | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WP05 | CWP01 | 3G4 | 112 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-DSS07 | - | PMS 230V busbar disconnector switch box Maintenance#01 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WC05 | CWC01 | 7G1,5 | 112 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-DSS07 | - | PMS 230V busbar disconnector switch box Maintenance#01 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WP07 | CWP01 | 3G4 | 112 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-DSS08 | - | PMS 230V busbar disconnector switch box Zone#02 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WC07 | CWC01 | 7G1,5 | 112 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-DSS08 | - | PMS 230V busbar disconnector switch box Zone#02 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WP09 | CWP01 | 3G4 | 138 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-DSS09 | - | PMS 230V busbar disconnector switch box Maintenance#02 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WC09 | CWC01 | 7G1,5 | 138 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-DSS09 | - | PMS 230V busbar disconnector switch box Maintenance#02 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WP11 | CWP01 | 3G4 | 138 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-DSS10 | - | PMS 230V busbar disconnector switch box Zone#03 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WC11 | CWC01 | 7G1,5 | 138 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-DSS10 | - | PMS 230V busbar disconnector switch box Zone#03 | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN00-PCP01-WE02 | CWE02 | SF/UTP | 80 | 6XV1870-2B | - | r43.62-3321-HGS-GEN00-CJB01 | - | Data rail communication junction box | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC20 | CWC01 | 7G1,5 | 140 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB11 | - | 3321 area technical room access local control box | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC21 | CWC01 | 3G1,5 | 68 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC01-XRA3101 | Billet area technical room safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC22 | CWC01 | 5G1,5 | 68 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC01-XRA3101 | Billet area technical room safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC23 | CWC01 | 7G1,5 | 72 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB12 | - | 3321 area HGS corridor access local control box | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC24 | CWC01 | 3G1,5 | 72 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC02-XRA3101 | HGS corridor main safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC25 | CWC01 | 5G1,5 | 72 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC02-XRA3101 | HGS corridor main safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC26 | CWC01 | 7G1,5 | 88 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB13 | - | 3322 area technical room access local control box | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC27 | CWC01 | 3G1,5 | 88 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC03-XRA3101 | Billet area technical room safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC28 | CWC01 | 5G1,5 | 88 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC03-XRA3101 | Billet area technical room safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC29 | CWC01 | 7G1,5 | 95 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB14 | - | 3322 area HGS corridor access local control box | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC30 | CWC01 | 3G1,5 | 95 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC04-XRA3101 | HGS corridor main safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC31 | CWC01 | 5G1,5 | 95 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC04-XRA3101 | HGS corridor main safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC32 | CWC01 | 7G1,5 | 115 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB15 | - | 3323 area technical room access local control box | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC33 | CWC01 | 3G1,5 | 115 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC05-XRA3101 | Billet area technical room safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC34 | CWC01 | 5G1,5 | 115 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC05-XRA3101 | Billet area technical room safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC35 | CWC01 | 7G1,5 | 120 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB16 | - | 3323 area HGS corridor access local control box | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC36 | CWC01 | 3G1,5 | 120 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC06-XRA3101 | HGS corridor main safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC37 | CWC01 | 5G1,5 | 120 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC06-XRA3101 | HGS corridor main safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC38 | CWC01 | 7G1,5 | 138 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB17 | - | 3324 area technical room access local control box | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC39 | CWC01 | 3G1,5 | 138 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC07-XRA3101 | Billet area technical room safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC40 | CWC01 | 5G1,5 | 138 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC07-XRA3101 | Billet area technical room safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC41 | CWC01 | 7G1,5 | 145 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB18 | - | 3324 area HGS corridor access local control box | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC42 | CWC01 | 3G1,5 | 145 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC08-XRA3101 | HGS corridor main safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WC43 | CWC01 | 5G1,5 | 145 | YSLY 300/500V | - | 3321-HGS-GEN00-ACC08-XRA3101 | HGS corridor main safety registry access | - | AIB
r43.62-3321-HGS-GEN00-DSS01 | - | r43.62-3321-HGS-GEN00-DSS01 | r43.62-3321-HGS-GEN00-DSS01-WP01 | CWP01 | 4G35 | 3 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PDR01 | - | Power data rail zone #01 | IFI
r43.62-3321-HGS-GEN00-DSS02 | - | r43.62-3321-HGS-GEN00-DSS02 | r43.62-3321-HGS-GEN00-DSS02-WP01 | CWP01 | 4G25 | 3 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PDR02 | - | Power data rail maintenace zone #01 | IFI
Data rail communication junction box | - | r43.62-3321-HGS-GEN00-CJB01 | r43.62-3321-HGS-GEN00-CJB01-WE01 | CWE02 | SMGM-VL-3000-QLS-N-RG316D (3M) | 3 | SMGM-VL-3000-QLS-N-RG316D (3M) | - | r43.62-3321-HGS-GEN00-CDR01 | Communication data rail |  | IFI
r43.62-3321-HGS-GEN00-DSS03 | - | r43.62-3321-HGS-GEN00-DSS03 | r43.62-3321-HGS-GEN00-DSS03-WP01 | CWP01 | 4G25 | 3 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PDR03 | - | Power data rail zone #02 | IFI
r43.62-3321-HGS-GEN00-DSS04 | - | r43.62-3321-HGS-GEN00-DSS04 | r43.62-3321-HGS-GEN00-DSS04-WP01 | CWP01 | 4G25 | 3 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PDR04 | - | Power data rail maintenace zone #02 | IFI
r43.62-3321-HGS-GEN00-DSS05 | - | r43.62-3321-HGS-GEN00-DSS05 | r43.62-3321-HGS-GEN00-DSS05-WP01 | CWP01 | 4G25 | 3 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PDR05 | - | Power data rail zone #03 | IFI
r43.62-3321-HGS-GEN00-DSS06 | - | r43.62-3321-HGS-GEN00-DSS06 | r43.62-3321-HGS-GEN00-DSS06-WP01 | CWP01 | 3G4 | 3 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PDR01 | - | Power data rail zone #01 | IFI
r43.62-3321-HGS-GEN00-DSS07 | - | r43.62-3321-HGS-GEN00-DSS07 | r43.62-3321-HGS-GEN00-DSS07-WP01 | CWP01 | 3G4 | 3 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PDR02 | - | Power data rail maintenace zone #01 | IFI
r43.62-3321-HGS-GEN00-DSS08 | - | r43.62-3321-HGS-GEN00-DSS08 | r43.62-3321-HGS-GEN00-DSS08-WP01 | CWP01 | 3G4 | 3 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PDR03 | - | Power data rail zone #02 | IFI
r43.62-3321-HGS-GEN00-DSS09 | - | r43.62-3321-HGS-GEN00-DSS09 | r43.62-3321-HGS-GEN00-DSS09-WP01 | CWP01 | 3G4 | 3 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PDR04 | - | Power data rail maintenace zone #02 | IFI
r43.62-3321-HGS-GEN00-DSS10 | - | r43.62-3321-HGS-GEN00-DSS10 | r43.62-3321-HGS-GEN00-DSS10-WP01 | CWP01 | 3G4 | 3 | RV-K 0,6/1kV | - | r43.62-3321-HGS-GEN00-PDR05 | - | Power data rail zone #03 | IFI
Power distribution rail | - | r43.62-3321-HGS-GEN00-PDR0x | r43.62-3321-HGS-TRS01-PIO01-WP20 | CWP01 | 4G10 | 3 | RV-K 0,6/1kV | - | r43.62-3321-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI
Power distribution rail | - | r43.62-3321-HGS-GEN00-PDR0x | r43.62-3321-HGS-TRS01-PIO01-WP21 | CWP01 | 4G10 | 3 | RV-K 0,6/1kV | - | r43.62-3321-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI
Power distribution rail | - | r43.62-3321-HGS-GEN00-PDR0x | r43.62-3321-HGS-TRS01-PIO01-WP22 | CWP01 | 2x1,5 | 3 | RV-K 0,6/1kV | - | r43.62-3321-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI
Power distribution rail | - | r43.62-3321-HGS-GEN00-PDR0x | r43.62-3321-HGS-TRS01-PIO01-WP23 | CWP01 | 2x1,5 | 3 | RV-K 0,6/1kV | - | r43.62-3321-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI
Communication data rail | - | r43.62-3321-HGS-GEN00-CDR01 | r43.62-3321-HGS-TRS01-PIO01-WE01 | CWE02 | SMGM-VL-3000-QLS-N-RG316D (3M) | 3 | SMGM-VL-3000-QLS-N-RG316D (3M) | - | r43.62-3321-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WP01 | CWP01 | 4G10 | 4 | RV-K 0,6/1kV | - | 3321-HGS-PMS01-ROT01-M01 | Magnet rotation motor | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WP02 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3321-HGS-ESR70-ACR01-M01A | Cooling blower motor | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WP03 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3321-HGS-ESR70-ACR01-M01B | Cooling blower motor | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WP04 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3321-HGS-TRS01-GEN01-M01 | Translation table motor | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WP05 | CWP01 | 3G2,5 | 4 | RV-K 0,6/1kV | - | 3321-HGS-TRS01-GEN01-M01 | Translation table motor | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WP06 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3321-HGS-ESR40-HYG01-M01 | Scissor elevator hydraulic pump motor | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC01 | CWC03 | TC K | 4 | SIL-FV-MM | - | 3321-HGS-PMS01-GEN01-TE1001 | Rotation thermocouple | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC02 | CWC02 | 2x1+SH | 5 | RC4V-K 300/500V | - | 3321-HGS-ESR70-ACR01-TS0711 | Cooling fan motor winding temperature M1A | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC03 | CWC02 | 2x1+SH | 5 | RC4V-K 300/500V | - | 3321-HGS-ESR70-ACR01-TS0712 | Cooling fan motor winding temperature M1B | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC04 | CWC02 | 7G1+SH | 5 | RC4V-K 300/500V | - | 3321-HGS-TRS01-GEN01-ZE1203 | Translation encoder | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC05 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3321-HGS-TRS01-MVP01-ZS1214 | PMS up | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC06 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3321-HGS-TRS01-MVP01-ZS1215 | PMS down | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC28 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3321-HGS-TRS01-GEN01-LS1201 | Traslation Limit Switch Forward | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC29 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3321-HGS-TRS01-GEN01-LS1202 | Traslation Limit Switch Backward | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC07 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3321-HGS-ESR40-HYG01-SV0410A | Solenoid valve PMS UP | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC08 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3321-HGS-ESR40-HYG01-SV0401B | Solenoid valve PMS DOWN | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC09 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3321-HGS-ESR40-GEN01-SV0401A | Solenoid valve PMS up feedback | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC10 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3321-HGS-ESR40-GEN01-SV0401B | Solenoid valve PMS down feedback | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC22 | CWC02 | 3G1+SH | 4 | RC4V-K 300/500V | - | 3321-HGS-ESR40-HYG01-PT0409 | Oil Filter Pressure Trasmitter | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC12 | CWC02 | 3G1+SH | 4 | RC4V-K 300/500V | - | 3321-HGS-ESR40-HYG01-LT0403 | Oil level switch Low | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC14 | CWC02 | 3G1+SH | 4 | RC4V-K 300/500V | - | 3321-HGS-ESR40-HYG01-LT0405 | Oil temperature trasmitter | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC15 | CWC02 | 5G1+SH | 5 | RC4V-K 300/500V | - | 3321-HGS-ESR40-HYG01-LT0406 | Oil pressure trasmitter #01 | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC16 | CWC02 | 5G1+SH | 5 | RC4V-K 300/500V | - | 3321-HGS-ESR40-HYG01-LT0407 | Oil pressure trasmitter #02 | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC17 | CWC02 | 5G1+SH | 5 | RC4V-K 300/500V | - | 3321-HGS-ESR40-HYG01-LT0408 | Oil pressure trasmitter #03 | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC18 | CWC02 | 12G1+SH | 4 | RC4V-K 300/500V | - | 3321-HGS-TRS01-GEN01-ZE1204A | Front safety scanner | - | IFI
TRS Power IO panel | - | r43.62-3321-HGS-TRS01-PIO01 | r43.62-3321-HGS-TRS01-PIO01-WC19 | CWC02 | 12G1+SH | 4 | RC4V-K 300/500V | - | 3321-HGS-TRS01-GEN01-ZE1204B | Back safety scanner | - | IFI
Power distribution rail | - | r43.62-3321-HGS-GEN00-PDR0x | r43.62-3322-HGS-TRS01-PIO01-WP20 | CWP01 | 4G10 | 3 | RV-K 0,6/1kV | - | r43.62-3322-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI
Power distribution rail | - | r43.62-3321-HGS-GEN00-PDR0x | r43.62-3322-HGS-TRS01-PIO01-WP21 | CWP01 | 4G10 | 3 | RV-K 0,6/1kV | - | r43.62-3322-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI
Power distribution rail | - | r43.62-3321-HGS-GEN00-PDR0x | r43.62-3322-HGS-TRS01-PIO01-WP22 | CWP01 | 2x1,5 | 3 | RV-K 0,6/1kV | - | r43.62-3322-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI
Power distribution rail | - | r43.62-3321-HGS-GEN00-PDR0x | r43.62-3322-HGS-TRS01-PIO01-WP23 | CWP01 | 2x1,5 | 3 | RV-K 0,6/1kV | - | r43.62-3322-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI
Communication data rail | - | r43.62-3321-HGS-GEN00-CDR01 | r43.62-3322-HGS-TRS01-PIO01-WE01 | CWE02 | SMGM-VL-3000-QLS-N-RG316D (3M) | 3 | SMGM-VL-3000-QLS-N-RG316D (3M) | - | r43.62-3322-HGS-TRS01-PIO01 | TRS Power IO panel | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WP01 | CWP01 | 4G10 | 4 | RV-K 0,6/1kV | - | 3322-HGS-PMS01-ROT01-M01 | Magnet rotation motor | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WP02 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3322-HGS-ESR70-ACR01-M01A | Cooling blower motor | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WP03 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3322-HGS-ESR70-ACR01-M01B | Cooling blower motor | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WP04 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3322-HGS-TRS01-GEN01-M01 | Translation table motor | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WP05 | CWP01 | 3G2,5 | 4 | RV-K 0,6/1kV | - | 3322-HGS-TRS01-GEN01-M01 | Translation table motor | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WP06 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3322-HGS-ESR40-HYG01-M01 | Scissor elevator hydraulic pump motor | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC02 | CWC02 | 2x1 | 5 | RC4V-k 0,6/1kV | - | 3322-HGS-ESR70-ACR01-TS0711 | Cooling fan motor winding temperature M1A | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC03 | CWC02 | 2x1 | 5 | RC4V-k 0,6/1kV | - | 3322-HGS-ESR70-ACR01-TS0712 | Cooling fan motor winding temperature M1B | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC04 | CWC02 | 7G1+SH | 5 | RC4V-k 0,6/1kV | - | 3322-HGS-TRS01-GEN01-ZE1203 | Translation encoder | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC05 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-TRS01-MVP01-ZS1214 | PMS up | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC06 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-TRS01-MVP01-ZS1215 | PMS down | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC28 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-TRS01-GEN01-LS1201 | Traslation Limit Switch Forward | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC29 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-TRS01-GEN01-LS1202 | Traslation Limit Switch Backward | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC07 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-ESR40-HYG01-SV0410A | Solenoid valve PMS UP | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC08 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-ESR40-HYG01-SV0401B | Solenoid valve PMS DOWN | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC09 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-ESR40-GEN01-SV0401A | Solenoid valve PMS up feedback | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC10 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-ESR40-GEN01-SV0401B | Solenoid valve PMS down feedback | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC22 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-ESR40-HYG01-PT0409 | Oil Filter Pressure Trasmitter | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC12 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-ESR40-HYG01-LT0403 | Oil level switch Low | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC14 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-ESR40-HYG01-LT0405 | Oil temperature trasmitter | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC15 | CWC02 | 5G1+SH | 5 | RC4V-k 0,6/1kV | - | 3322-HGS-ESR40-HYG01-LT0406 | Oil pressure trasmitter #01 | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC16 | CWC02 | 5G1+SH | 5 | RC4V-k 0,6/1kV | - | 3322-HGS-ESR40-HYG01-LT0407 | Oil pressure trasmitter #02 | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC17 | CWC02 | 5G1+SH | 5 | RC4V-k 0,6/1kV | - | 3322-HGS-ESR40-HYG01-LT0408 | Oil pressure trasmitter #03 | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC18 | CWC01 | 12G1 | 4 | YSLY 300/500V | - | 3322-HGS-TRS01-GEN01-ZE1204A | Front safety scanner | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC19 | CWC01 | 12G1 | 4 | YSLY 300/500V | - | 3322-HGS-TRS01-GEN01-ZE1204B | Back safety scanner | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WP01 | CWP01 | 4G10 | 4 | RV-K 0,6/1kV | - | 3322-HGS-PMS01-ROT01-M01 (VFPS03) | PMS Rotation motor | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WP02 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3322-HGS-ESR70-ACR01-M01A (D03) | Cooling fan motor #A | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WP03 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3322-HGS-ESR70-ACR01-M01B (D03) | Cooling fan motor #B | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WP04 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3322-HGS-TRS01-GEN01-M01 (VFPS04) | Platform Translation motor | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WP05 | CWP01 | 3G2,5 | 4 | RV-K 0,6/1kV | - | 3322-HGS-TRS01-GEN01-M01 (VFPS04) | Platform Translation motor BREAK | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WP06 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3322-HGS-ESR40-HYG01-M01 (D03) | Hydraulic group pump motor | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PCP01-WC01 | CWC03 | TC K | 4 | K SIL-FV-MM | - | 3322-HGS-PMS01-GEN01-TE1001 | Rotation thermocouple | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC05 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-TRS01-MVP01-ZS1214 | PMS up | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC06 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-TRS01-MVP01-ZS1215 | PMS down | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC28 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-TRS01-GEN01-LS1201 | Traslation Limit Switch Forward | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC29 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-TRS01-GEN01-LS1202 | Traslation Limit Switch Backward | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC07 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-ESR40-HYG01-SV0410A | Solenoid valve PMS UP | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC08 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-ESR40-HYG01-SV0401B | Solenoid valve PMS DOWN | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC09 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-ESR40-GEN01-SV0401A | Solenoid valve PMS up feedback | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC10 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-ESR40-GEN01-SV0401B | Solenoid valve PMS down feedback | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC22 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-ESR40-HYG01-PT0409 | Oil Filter Pressure Trasmitter | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC12 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-ESR40-HYG01-LT0403 | Oil level switch Low | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PIO01-WC14 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3322-HGS-ESR40-HYG01-LT0405 | Oil temperature trasmitter | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PCP01-WC18 | CWC01 | 12G1 | 4 | YSLY 300/500V | - | 3322-HGS-TRS01-GEN01-ZE1204A | Front safety scanner | - | IFI
TRS Power IO panel | - | r43.62-3322-HGS-TRS01-PIO01 | r43.62-3322-HGS-TRS01-PCP01-WC19 | CWC01 | 12G1 | 4 | YSLY 300/500V | - | 3322-HGS-TRS01-GEN01-ZE1204B | Back safety scanner | - | IFI
Power distribution rail | - | r43.62-3321-HGS-GEN00-PDR0x | r43.62-3323-HGS-TRS01-PIO01-WP20 | CWP01 | 4G10 | 3 | RV-K 0,6/1kV | - | r43.62-3323-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI
Power distribution rail | - | r43.62-3321-HGS-GEN00-PDR0x | r43.62-3323-HGS-TRS01-PIO01-WP21 | CWP01 | 4G10 | 3 | RV-K 0,6/1kV | - | r43.62-3323-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI
Power distribution rail | - | r43.62-3321-HGS-GEN00-PDR0x | r43.62-3323-HGS-TRS01-PIO01-WP22 | CWP01 | 2x1,5 | 3 | RV-K 0,6/1kV | - | r43.62-3323-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI
Power distribution rail | - | r43.62-3321-HGS-GEN00-PDR0x | r43.62-3323-HGS-TRS01-PIO01-WP23 | CWP01 | 2x1,5 | 3 | RV-K 0,6/1kV | - | r43.62-3323-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI
Communication data rail | - | r43.62-3321-HGS-GEN00-CDR01 | r43.62-3323-HGS-TRS01-PIO01-WE01 | CWE02 | SMGM-VL-3000-QLS-N-RG316D (3M) | 3 | SMGM-VL-3000-QLS-N-RG316D (3M) | - | r43.62-3323-HGS-TRS01-PIO01 | - | TRS Power IO panel | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PIO01-WP01 | CWP01 | 4G10 | 4 | RV-K 0,6/1kV | - | 3323-HGS-PMS01-ROT01-M01 | Magnet rotation motor | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PIO01-WP02 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3323-HGS-ESR70-ACR01-M01A | Cooling blower motor | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PIO01-WP03 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3323-HGS-ESR70-ACR01-M01B | Cooling blower motor | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PIO01-WP04 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3323-HGS-TRS01-GEN01-M01 | Translation table motor | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PIO01-WP05 | CWP01 | 3G2,5 | 4 | RV-K 0,6/1kV | - | 3323-HGS-TRS01-GEN01-M01 | Translation table motor | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PIO01-WP06 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3323-HGS-ESR40-HYG01-M01 | Scissor elevator hydraulic pump motor | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC01 | CWC03 | TC K | 4 | K SIL-FV-MM | - | 3323-HGS-PMS01-GEN01-TE1001 | Rotation thermocouple | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC02 | CWC02 | 2x1 | 5 | RC4V-k 0,6/1kV | - | 3323-HGS-ESR70-ACR01-TS0711 | Cooling fan motor winding temperature M1A | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC03 | CWC02 | 2x1 | 5 | RC4V-k 0,6/1kV | - | 3323-HGS-ESR70-ACR01-TS0712 | Cooling fan motor winding temperature M1B | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC04 | CWC02 | 7G1+SH | 5 | RC4V-k 0,6/1kV | - | 3323-HGS-TRS01-GEN01-ZE1203 | Translation encoder | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC05 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3323-HGS-TRS01-MVP01-ZS1214 | PMS up | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC06 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3323-HGS-TRS01-MVP01-ZS1215 | PMS down | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC28 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3323-HGS-TRS01-GEN01-LS1201 | Traslation Limit Switch Forward | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC29 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3323-HGS-TRS01-GEN01-LS1202 | Traslation Limit Switch Backward | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC07 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3323-HGS-ESR40-HYG01-SV0410A | Solenoid valve PMS UP | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC08 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3323-HGS-ESR40-HYG01-SV0401B | Solenoid valve PMS DOWN | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC09 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3323-HGS-ESR40-GEN01-SV0401A | Solenoid valve PMS up feedback | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC10 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3323-HGS-ESR40-GEN01-SV0401B | Solenoid valve PMS down feedback | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC22 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3323-HGS-ESR40-HYG01-PT0409 | Oil Filter Pressure Trasmitter | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC12 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3323-HGS-ESR40-HYG01-LT0403 | Oil level switch Low | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC14 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 3323-HGS-ESR40-HYG01-LT0405 | Oil temperature trasmitter | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC15 | CWC02 | 5G1+SH | 5 | RC4V-k 0,6/1kV | - | 3323-HGS-ESR40-HYG01-LT0406 | Oil pressure trasmitter #01 | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC16 | CWC02 | 5G1+SH | 5 | RC4V-k 0,6/1kV | - | 3323-HGS-ESR40-HYG01-LT0407 | Oil pressure trasmitter #02 | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC17 | CWC02 | 5G1+SH | 5 | RC4V-k 0,6/1kV | - | 3323-HGS-ESR40-HYG01-LT0408 | Oil pressure trasmitter #03 | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC18 | CWC01 | 12G1 | 4 | YSLY 300/500V | - | 3323-HGS-TRS01-GEN01-ZE1204A | Front safety scanner | - | IFI
TRS Power IO panel | - | r43.62-3323-HGS-TRS01-PIO01 | r43.62-3323-HGS-TRS01-PCP01-WC19 | CWC01 | 12G1 | 4 | YSLY 300/500V | - | 3323-HGS-TRS01-GEN01-ZE1204B | Back safety scanner | - | IFI
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC01 | CWC01 | 7G1,5 | 80 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB01 | HGS corridor maintenance safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC02 | CWC01 | 7G1,5 | 112 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB02 | HGS corridor maintenance safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC03 | CWC01 | 7G1,5 | 112 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB03 | HGS corridor maintenance safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC04 | CWC01 | 7G1,5 | 136 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB04 | HGS corridor maintenance safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC05 | CWC01 | 7G1,5 | 138 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB05 | HGS corridor maintenance safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC06 | CWC01 | 7G1,5 | 78 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB06 | HGS corridor maintenance safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC07 | CWC01 | 7G1,5 | 112 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB07 | HGS corridor maintenance safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN00-PCP01 | r41.62-3311-HGS-GEN01-PCP01-WC08 | CWC01 | 7G1,5 | 112 | YSLY 300/500V | - | r43.62-3321-HGS-GEN00-LCB08 | HGS corridor maintenance safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN01-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WP09 | CWC01 | 7G1,5 | 138 | YSLY 300/500V | - | r43.62-3321-HGS-GEN01-LCB09 | HGS corridor maintenance safety registry access | - | AIB
Strip cast electrical room #01 | - | r43.62-3321-HGS-GEN01-PCP01 | r43.62-3321-HGS-GEN01-PCP01-WP10 | CWC01 | 7G1,5 | 138 | YSLY 300/500V | - | r43.62-3321-HGS-GEN01-LCB10 | HGS corridor maintenance safety registry access | - | AIB