## Cover
Client: |  | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
Cover
CUSTOMER: |  | ALINVEST | PREPARED: | AIBI
PROJECT CODE: |  | E2558 | REVIEWED: | ANSA
PROJECT NAME: |  | ALFAGEN | DATE: | 2025/12/02
CONTRACTOR DOC. CODE: |  | 2558-3323-TMT-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: |  | 2558-3323-TMT-E-LST-CBLS | PAGE: | 01 of 10
REVISION CONTROL
REV | DATE | DESCRIPTON |  | PAGE
A | 2025/12/02 | Issue for information |  | 1-10
B
C
D
E
F
G
H
I
J
K
L
M
N
O
P
Q
R
S
T
U
V
W
X
Y
Z
AA
AB
AC
AD
AE
The drawing(s), document(s) and the information contained herein are the property of INDUSTRIAL FURNACES INSERTEC. And they shall not be disclosed, reproduced or used in any manner without the prior written consent of INDUSTRIAL FURNACES INSERTEC. Offenders will be held liable for the payment of damages.

## Table of Contents
Client: |  | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
Table of contents
CUSTOMER: |  | ALINVEST | PREPARED: | AIBI
PROJECT CODE: |  | E2558 | REVIEWED: | ANSA
PROJECT NAME: |  | ALFAGEN | DATE: | 2025/12/02
CONTRACTOR DOC. CODE: |  | 2558-3323-TMT-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: |  | 2558-3323-TMT-E-LST-CBLS | PAGE: | 02 of 10
Table of contents
SEC | DESCRIPTON |  |  | PAGE
0 | Cover |  |  | 1
1 | Table of contents |  |  | 2
2 | Definitions |  |  | 3
3 | Equipment cable list |  |  | 4-10
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
The drawing(s), document(s) and the information contained herein are the property of INDUSTRIAL FURNACES INSERTEC. And they shall not be disclosed, reproduced or used in any manner without the prior written consent of INDUSTRIAL FURNACES INSERTEC. Offenders will be held liable for the payment of damages.

## Definitions
Client: | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
DEFINITIONS
CUSTOMER: | ALINVEST | PREPARED: | AIBI
PROJECT CODE: | E2558 | REVIEWED: | ANSA
PROJECT NAME: | ALFAGEN | DATE: | 2025/12/02
CONTRACTOR DOC. CODE: | 2558-3323-TMT-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: | 2558-3323-TMT-E-LST-CBLS | PAGE: | 03 of 10
MAIN DEFINITIONS
== -
= -
++ -
+ -
Description -
IME (Complete) -
Tag - For more detail, please refer to B001-B002-GEN-E-PRC-NPOS-R09 Numbering procedure for electrical objects and signals document.
Category - For more detail, please refer to B001-B002-GNL-E-SPC-INCC-R02 Technical specification for cables and cable trays document.
Type - Cable type according to conductor number, section, shield, etc
Length - Estimated lenght of the given cable.
Page - Page number realted to the electrical schematics. Refer to: B001-B002-B003-E-DWG-ESCH-R00 Equipment electrical schematics
Function -
Remarks - Notes to be considered.
Revision change comments - Revision change reason comments.

## Equipment cable list
Client: | CUSTOMER: | ALINVEST |  | EQUIPMENT CABLE LIST | [7 empty] | PREPARED: | AIBI | Contractor:
ALINVEST | PROJECT CODE: | E2558 | [9 empty] | REVIEWED: | ANSA
| PROJECT NAME: | ALFAGEN | [9 empty] | DATE: | 2025/12/02
| CONTRACTOR DOC. CODE: | 2558-3323-TMT-E-LST-CBLS | [9 empty] | REVISION: | A
| CUSTOMER DOC. CODE: | 2558-3323-TMT-E-LST-CBLS | [9 empty] | PAGE: | 04/10 of 10
SOURCE |  |  | CABLE | [5 empty] | DESTINATION |  |  | OTHERS
Location Description | Instrument Description | Device Tag | Tag | Category | Type | Length [m] | Cable Reference | Route | Device Tag | Instrument Description | Location Description | Scope of Supply | Remarks | Revision Change Comment
T145.31 | - | r45.31 | WL45.31.R1 | CWP01 | 1x240 | TBD BY CLIENT | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PCP01 | - | TMT main power control panel | AIB | - | -
T145.31 | - | r45.31 | WL45.31.R2 | CWP01 | 1x240 | TBD BY CLIENT | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PCP01 | - | TMT main power control panel | AIB | - | -
T145.31 | - | r45.31 | WL45.31.S1 | CWP01 | 1x240 | TBD BY CLIENT | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PCP01 | - | TMT main power control panel | AIB | - | -
T145.31 | - | r45.31 | WL45.31.S2 | CWP01 | 1x240 | TBD BY CLIENT | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PCP01 | - | TMT main power control panel | AIB | - | -
T145.31 | - | r45.31 | WL45.31.T1 | CWP01 | 1x240 | TBD BY CLIENT | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PCP01 | - | TMT main power control panel | AIB | - | -
T145.31 | - | r45.31 | WL45.31.T2 | CWP01 | 1x240 | TBD BY CLIENT | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PCP01 | - | TMT main power control panel | AIB | - | -
T145.31 | - | r45.31 | WL45.31.P1 | CWP01 | 1x240 PE | TBD BY CLIENT | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PCP01 | - | TMT main power control panel | AIB | - | -
T145.31 | - | r45.31 | WL45.31.L1 | CWP01 | 3G4 | TBD BY CLIENT | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PCP01 | - | TMT main power control panel | AIB | - | -
APU Power Distribution Panel | - | r45.31-0323-GEN-APU01-PDP01 | r45.31-0323-GEN-APU01-PDP01-WP01 | CWP01 | 3G2,5 | 14 | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PCP01 | - | TMT main power control panel | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP01 | CWP01 | 4G16 | 115 | RV-K 0,6/1kV | - | r45.31-3323-SFS-GEN01-PCP01 | - | STAS RFI power control panel | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP02 | CWP01 | 4G2,5 | 14 | RV-K 0,6/1kV | - | r45.31-0323-GEN-APU01-PDP01 | - | APU Power Distribution Panel | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP03 | CWP01 | 3G2,5 | 101 | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-LCP01 | - | TMT general local control panel | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP04 | CWP01 | 3G2,5 | 101 | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-LCP01 | - | TMT general local control panel | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP05 | CWP01 | 3G4 | 113 | RV-K 0,6/1kV | - | r45.31-3323-TMT-ESR00-RIO01 | - | TMT energy sources remote I/O: fans technical room | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP06 | CWP01 | 3G4 | 113 | RV-K 0,6/1kV | - | r45.31-3323-TMT-ESR00-RIO01 | - | TMT energy sources remote I/O: fans technical room | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP07 | CWP01 | 3G2,5 | 88 | RV-K 0,6/1kV | - | r45.31-3323-TMT-ESR00-RIO02 | - | TMT energy sources remote I/O: main gas & O2 skid | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP08 | CWP01 | 3G2,5 | 88 | RV-K 0,6/1kV | - | r45.31-3323-TMT-ESR00-RIO02 | - | TMT energy sources remote I/O: main gas & O2 skid | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WE03 | CWE02 | SF/UTP | 88 | 6XV1840-2AH10 | - | r45.31-3323-TMT-ESR00-RIO02 | - | TMT energy sources remote I/O: main gas & O2 skid | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP10 | CWP02 | 4G16+SH | 105 | RC4V-K 0,6/1kV | - | r45.31-3323-TMT-ESR10-DSS01 | - | Combustion Fan disconnector switch | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP11 | CWP02 | 4G4+SH | 105 | RC4V-K 0,6/1kV | - | r45.31-3323-TMT-ESR70-DSS01 | - | Pilot Combustion Fan disconnector switch | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP12 | CWP02 | 4G35+SH | 105 | RC4V-K 0,6/1kV | - | r45.31-3323-TMT-ESR90-DSS01 | - | Exhaust fan disconnector switch | AIB | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC09 | CWC01 | 2x1 | 15 | YSLY 300/500V | - | r45.31-3323-TMT-ESR10-DSS01 | - | Combustion Fan disconnector switch | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC23 | CWC01 | 2x1 | 15 | YSLY 300/500V | - | r45.31-3323-TMT-ESR70-DSS01 | - | Pilot Combustion Fan disconnector switch | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC38 | CWC01 | 2x1 | 15 | YSLY 300/500V | - | r45.31-3323-TMT-ESR90-DSS01 | - | Exhaust fan disconnector switch | IFI | - | -
Combustion Fan disconnector switch | - | r45.31-3323-TMT-ESR10-DSS01 | r45.31-3323-TMT-ESR10-DSS01-WP01 | CWP02 | 4G16+SH | 4 | RC4V-K 0,6/1kV | - | 3323-TMT-ESR10-CBF01-M01 | Combustion Fan | - | AIB | - | -
Pilot Combustion Fan disconnector switch | - | r45.31-3323-TMT-ESR70-DSS01 | r45.31-3323-TMT-ESR70-DSS01-WP01 | CWP02 | 4G4+SH | 4 | RC4V-K 0,6/1kV | - | 3323-TMT-ESR70-AAF01-M01 | Pilot Combustion Fan | - | AIB | - | -
Exhaust fan disconnector switch | - | r45.31-3323-TMT-ESR90-DSS01 | r45.31-3323-TMT-ESR90-DSS01-WP01 | CWP02 | 4G35+SH | 4 | RC4V-K 0,6/1kV | - | 3323-TMT-ESR90-EXF01-M01 | Exhaust Fan | - | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP15 | CWP01 | 3G2,5 | 107 | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PDP01 | - | Plant cable routing power distribution panel | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP16 | CWP01 | 4G2,5 | 107 | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PDP01 | - | Plant cable routing power distribution panel | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP17 | CWP01 | 4G2,5 | 107 | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PDP01 | - | Plant cable routing power distribution panel | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP18 | CWP01 | 4G2,5 | 107 | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PDP01 | - | Plant cable routing power distribution panel | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP20 | CWP01 | 3G4 | 107 | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PDP01 | - | Plant cable routing power distribution panel | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP21 | CWP01 | 3G4 | 107 | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PDP01 | - | Plant cable routing power distribution panel | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP22 | CWP01 | 3G4 | 107 | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PDP01 | - | Plant cable routing power distribution panel | AIB | - | -
TMT main power control panel | - | r45.31-3323-TMT-GEN01-PCP01 | r45.31-3323-TMT-GEN01-PCP01-WP23 | CWP01 | 3G4 | 107 | RV-K 0,6/1kV | - | r45.31-3323-TMT-GEN01-PDP01 | - | Plant cable routing power distribution panel | AIB | - | -
Plant cable routing power distribution panel | - | r45.31-3323-TMT-GEN01-PDP01 | r45.31-3323-TMT-GEN01-PDP01-WP01 | CWP01 | 4G2,5 | 30 | RV-K 0,6/1kV | - | r45.31-3323-TMT-MCH01-DSS01 | - | Bath thermocouple retraction motor disconnector switch | IFI | - | -
Plant cable routing power distribution panel | - | r45.31-3323-TMT-GEN01-PDP01 | r45.31-3323-TMT-GEN01-PDP01-WP02 | CWP01 | 4G2,5 | 25 | RV-K 0,6/1kV | - | r45.31-3323-TMT-CVT01-PCP01 | - | Monitoring camera power control panel #01 | IFI | - | -
Plant cable routing power distribution panel | - | r45.31-3323-TMT-GEN01-PDP01 | r45.31-3323-TMT-GEN01-PDP01-WP03 | CWP01 | 4G2,5 | 23 | RV-K 0,6/1kV | - | r45.31-3323-TMT-CVT01-PCP02 | - | Monitoring camera power control panel #02 | IFI | - | -
Plant cable routing power distribution panel | - | r45.31-3323-TMT-GEN01-PDP01 | r45.31-3323-TMT-GEN01-PDP01-WP05 | CWP01 | 3G4 | 25 | RV-K 0,6/1kV | - | r45.31-3323-TMT-CBS01-RIO01 | - | Combustion area remote IO | IFI | - | -
Plant cable routing power distribution panel | - | r45.31-3323-TMT-GEN01-PDP01 | r45.31-3323-TMT-GEN01-PDP01-WP06 | CWP01 | 3G4 | 25 | RV-K 0,6/1kV | - | r45.31-3323-TMT-CBS01-RIO01 | - | Combustion area remote IO | IFI | - | -
Plant cable routing power distribution panel | - | r45.31-3323-TMT-GEN01-PDP01 | r45.31-3323-TMT-GEN01-PDP01-WP07 | CWP01 | 3G4 | 23 | RV-K 0,6/1kV | - | r45.31-3323-TMT-MCH01-RIO01 | - | Auxiliaries remote IO | IFI | - | -
Plant cable routing power distribution panel | - | r45.31-3323-TMT-GEN01-PDP01 | r45.31-3323-TMT-GEN01-PDP01-WP08 | CWP01 | 3G4 | 23 | RV-K 0,6/1kV | - | r45.31-3323-TMT-MCH01-RIO01 | - | Auxiliaries remote IO | IFI | - | -
Bath thermocouple retraction motor disconnector switch | - | r45.31-3323-TMT-MCH01-DSS01 | r45.31-3323-TMT-MCH01-DSS01-WP01 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | 3323-TMT-MCH01-TEX01-M01 | Bath thermocouple retraction motor | - | IFI | - | -
Bath TC local control box | - | r45.31-3323-TMT-MCH01-LCB03 | r45.31-3323-TMT-MCH01-LCB03-WC01 | CWC01 | 2x1 | 4 | YSLY 300/500V | - | r45.31-3323-TMT-MCH01-DSS01 | - | Bath thermocouple retraction motor disconnector switch | IFI | - | -
TMT general local control panel | - | r45.31-3323-TMT-GEN01-LCP01 | r45.31-3323-TMT-GEN01-LCP01-WE01 | CWE02 | SF/UTP | 6 | 6XV1840-2AH10 | - | r45.31-3323-TMT-GEN01-PDP01 | - | Plant cable routing power distribution panel | IFI | - | -
Plant cable routing power distribution panel | - | r45.31-3323-TMT-GEN01-PDP01 | r45.31-3323-TMT-GEN01-PDP01-WE01 | CWE02 | SF/UTP | 25 | 6XV1840-2AH10 | - | r45.31-3323-TMT-CBS01-RIO01 | - | Combustion area remote IO | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WE01 | CWE02 | SF/UTP | 113 | 6XV1840-2AH10 | - | r45.31-3323-TMT-GEN01-PCP01 | - | TMT main power control panel | AIB | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC01 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR10-GEN01-PS0101 | Comb. air low pressure switch SF | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC02 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR10-GEN01-PS0102 | Comb. air low pressure switch SF | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC03 | CWC02 | 4x0,34+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR10-CBF01-VT0101 | DE bearing vibration sensor | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC04 | CWC02 | 4x0,34+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR10-CBF01-VT0102 | NDE bearing vibration sensor | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC05 | CWC02 | 4x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR10-CBF01-TE0101 | DE bearing temperature | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC06 | CWC02 | 4x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR10-CBF01-TE0102 | NDE bearing temperature | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC07 | CWC02 | 4x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR10-CBF01-TE0103 | Motor temperature | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC08 | CWC02 | 2x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR10-CBF01-TE0104 | Motor winding temperature | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC15 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR70-GEN01-PS0701 | Addition air low pressure switch SF | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC16 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR70-GEN01-PS0702 | Addition air low pressure switch SF | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC17 | CWC02 | 4x0,34+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR70-AAF01-VT0701 | DE bearing vibration sensor | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC18 | CWC02 | 4x0,34+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR70-AAF01-VT0702 | NDE bearing vibration sensor | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC19 | CWC02 | 4x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR70-AAF01-TE0701 | DE bearing temperature | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC20 | CWC02 | 4x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR70-AAF01-TE0702 | NDE bearing temperature | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC21 | CWC02 | 4x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR70-AAF01-TE0703 | Motor temperature | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC22 | CWC02 | 2x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR70-AAF01-TE0704 | Motor winding temperature | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC30 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR90-GEN01-PS0901 | Exhaust air low pressure switch SF | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC31 | CWC03 | TC K | 10 | SIL-FV-MM | - | 3323-TMT-ESR90-GEN01-TE0901 | Exhaust air temperature | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC32 | CWC02 | 4x0,34+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR90-EXF01-VT0901 | DE bearing vibration sensor | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC33 | CWC02 | 4x0,34+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR90-EXF01-VT0902 | NDE bearing vibration sensor | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC34 | CWC02 | 4x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR90-EXF01-TE0901 | DE bearing temperature | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC35 | CWC02 | 4x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR90-EXF01-TE0902 | NDE bearing temperature | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC36 | CWC02 | 4x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR90-EXF01-TE0903 | Motor temperature | - | IFI | - | -
TMT energy sources remote I/O: fans technical room | - | r45.31-3323-TMT-ESR00-RIO01 | r45.31-3323-TMT-ESR00-RIO01-WC37 | CWC02 | 2x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR90-EXF01-TE0904 | Motor winding temperature | - | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WE01 | CWE02 | SF/UTP | 50 | 6XV1840-2AH10 | - | r45.31-3323-TMT-GEN01-LCP01 | - | TMT general local control panel | IFI | - | -
TMT general local control panel | - | r45.31-3323-TMT-GEN01-LCP01 | r45.31-3323-TMT-GEN01-LCP01-WC01 | CWC01 | 24G1 | 15 | YSLY 300/500V | - | r45.31-3323-TMT-MCH01-LCB05 | - | Tilting & spout local control box | IFI | - | -
TMT general local control panel | - | r45.31-3323-TMT-GEN01-LCP01 | r45.31-3323-TMT-GEN01-LCP01-WC02 | CWC02 | 6G1+SH | 15 | RC4V-K 300/500V | - | r45.31-3323-TMT-MCH01-LCB05 | - | Tilting & spout local control box | IFI | - | -
TMT general local control panel | - | r45.31-3323-TMT-GEN01-LCP01 | r45.31-3323-TMT-GEN01-LCP01-WC03 | CWC01 | 24G1 | 40 | YSLY 300/500V | - | r45.31-3323-MHL-LAN01-IJB01 | - | Dam instrumentation juntion box | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WC01 | CWC01 | 24G1 | 6 | YSLY 300/500V | - | r45.31-3323-TMT-ESR20-IJB01 | - | Combustion gas main skid instrumentation junction box | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WP01 | CWP01 | 3G1,5 | 6 | RV-K 0,6/1kV | - | r45.31-3323-TMT-ESR20-IJB01 | - | Combustion gas main skid instrumentation junction box | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WP02 | CWP01 | 3G1,5 | 6 | RV-K 0,6/1kV | - | r45.31-3323-TMT-ESR20-IJB01 | - | Combustion gas main skid instrumentation junction box | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WC05 | CWC01 | 24G1 | 6 | YSLY 300/500V | - | r45.31-3323-TMT-ESR50-IJB01 | - | Compressed air main skid instrumentation junction box | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WC07 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR50-SKD04-PS0501 | O2 cabinet comp. air low press. switch | - | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WC08 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR30-SKD01-PT0301 | O2 cabinet oxygen dif. Pressure | - | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WC09 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR30-SKD01-PS0301 | O2 cabinet oxygen low pressure | - | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WC10 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR30-SKD01-PS0302 | O2 cabinet oxygen high pressure | - | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WC11 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR30-SKD01-FT0301 | O2 cabinet oxygen flow meter | - | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WC12 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR30-SKD01-SV0301 | O2 cabinet oxygen pilot valve | - | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WC13 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR30-SKD01-ACC0301 | O2 cabinet oxygen pilot valve limit switch box | - | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WC14 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR30-SKD01-ZS0301 | O2 cabinet positioner | - | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WC20 | CWC01 | 24G1 | 30 | YSLY 300/500V | - | r45.31-3323-TMT-MCH01-IJB03 | - | Chimney instrumentation junction box | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WC21 | CWC02 | 24G1+SH | 30 | RC4V-K 300/500V | - | r45.31-3323-TMT-MCH01-IJB03 | - | Chimney instrumentation junction box | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WC23 | CWC01 | 12G1 | 30 | YSLY 300/500V | - | r45.31-3323-TMT-MCH01-IJB03 | - | Chimney instrumentation junction box | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WP03 | CWP01 | 3G1,5 | 30 | RV-K 0,6/1kV | - | r45.31-3323-TMT-MCH01-IJB03 | - | Chimney instrumentation junction box | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WP04 | CWP01 | 3G1,5 | 30 | RV-K 0,6/1kV | - | r45.31-3323-TMT-MCH01-IJB03 | - | Chimney instrumentation junction box | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WP05 | CWP01 | 3G1,5 | 30 | RV-K 0,6/1kV | - | r45.31-3323-TMT-MCH01-IJB03 | - | Chimney instrumentation junction box | IFI | - | -
TMT energy sources remote I/O: main gas & O2 skid | - | r45.31-3323-TMT-ESR00-RIO02 | r45.31-3323-TMT-ESR00-RIO02-WC25 | CWC03 | TC K | 10 | SIL-FV-MM | - | 3323-TMT-MCH01-CHY01-TE1101 | Furnace exhaust temperature | - | IFI | - | -
Tilting & spout local control box | - | r45.31-3323-TMT-MCH01-LCB05 | r45.31-3323-TMT-MCH01-IJB05-WC01 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-MHL-LAN01-MLM01-LS2101 | Launder level switch | - | IFI | - | -
Tilting & spout local control box | - | r45.31-3323-TMT-MCH01-LCB05 | r45.31-3323-TMT-MCH01-IJB05-WC02 | CWC02 | 5x1+SH | 10 | RC4V-K 300/500V | - | 3323-MHL-LAN01-MLM01-LT2101 | Launder level transmitter | - | IFI | - | -
Dam instrumentation juntion box | - | r45.31-3323-MHL-LAN01-IJB01 | r45.31-3323-MHL-LAN01-IJB01-WC01 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-MHL-LAN01-GAT01-SV2101A | Solenoid valve | - | IFI | - | -
Dam instrumentation juntion box | - | r45.31-3323-MHL-LAN01-IJB01 | r45.31-3323-MHL-LAN01-IJB01-WC02 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-MHL-LAN01-GAT01-SV2101B | Solenoid valve | - | IFI | - | -
Dam instrumentation juntion box | - | r45.31-3323-MHL-LAN01-IJB01 | r45.31-3323-MHL-LAN01-IJB01-WC03 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-MHL-LAN01-GAT01-ZS2101A | Launder gate #01 open limit switch | - | IFI | - | -
Dam instrumentation juntion box | - | r45.31-3323-MHL-LAN01-IJB01 | r45.31-3323-MHL-LAN01-IJB01-WC04 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-MHL-LAN01-GAT01-ZS2101B | Launder gate #01 open limit switch | - | IFI | - | -
Dam instrumentation juntion box | - | r45.31-3323-MHL-LAN01-IJB01 | r45.31-3323-MHL-LAN01-IJB01-WC05 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-MHL-LAN01-GAT02-SV2101A | Solenoid valve | - | IFI | - | -
Dam instrumentation juntion box | - | r45.31-3323-MHL-LAN01-IJB01 | r45.31-3323-MHL-LAN01-IJB01-WC06 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-MHL-LAN01-GAT02-SV2101B | Solenoid valve | - | IFI | - | -
Dam instrumentation juntion box | - | r45.31-3323-MHL-LAN01-IJB01 | r45.31-3323-MHL-LAN01-IJB01-WC07 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-MHL-LAN01-GAT02-ZS2101A | Launder gate #02 open limit switch | - | IFI | - | -
Dam instrumentation juntion box | - | r45.31-3323-MHL-LAN01-IJB01 | r45.31-3323-MHL-LAN01-IJB01-WC08 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-MHL-LAN01-GAT02-ZS2101B | Launder gate #02 open limit switch | - | IFI | - | -
Combustion gas main skid instrumentation junction box | - | r45.31-3323-TMT-ESR20-IJB01 | r45.31-3323-TMT-ESR20-IJB01-WC01 | CWC02 | 4G1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR20-SKD01-PDT0201 | Dif. press. transmitter | - | IFI | - | -
Combustion gas main skid instrumentation junction box | - | r45.31-3323-TMT-ESR20-IJB01 | r45.31-3323-TMT-ESR20-IJB01-WC02 | CWC02 | 3G1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ESR20-SKD01-FQ0201 | Quantometer | - | IFI | - | -
Combustion gas main skid instrumentation junction box | - | r45.31-3323-TMT-ESR20-IJB01 | r45.31-3323-TMT-ESR20-IJB01-WC03 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR20-SKD01-PS0201 | Main gas low pressure switch SF | - | IFI | - | -
Combustion gas main skid instrumentation junction box | - | r45.31-3323-TMT-ESR20-IJB01 | r45.31-3323-TMT-ESR20-IJB01-WC04 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR20-SKD01-PS0202 | Main gas low pressure switch SF | - | IFI | - | -
Combustion gas main skid instrumentation junction box | - | r45.31-3323-TMT-ESR20-IJB01 | r45.31-3323-TMT-ESR20-IJB01-WC05 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR20-SKD01-PS0203 | Main gas high pressure switch SF | - | IFI | - | -
Combustion gas main skid instrumentation junction box | - | r45.31-3323-TMT-ESR20-IJB01 | r45.31-3323-TMT-ESR20-IJB01-WC06 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR20-SKD01-PS0204 | Main gas high pressure switch SF | - | IFI | - | -
Combustion gas main skid instrumentation junction box | - | r45.31-3323-TMT-ESR20-IJB01 | r45.31-3323-TMT-ESR20-IJB01-WC07 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR20-SKD01-PS0205 | Tighness control pressure switch SF | - | IFI | - | -
Combustion gas main skid instrumentation junction box | - | r45.31-3323-TMT-ESR20-IJB01 | r45.31-3323-TMT-ESR20-IJB01-WC08 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR20-SKD01-PS0206 | Ignition gas low pressure switch SF | - | IFI | - | -
Combustion gas main skid instrumentation junction box | - | r45.31-3323-TMT-ESR20-IJB01 | r45.31-3323-TMT-ESR20-IJB01-WC09 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR20-SKD01-PS0207 | Ignition gas low pressure switch SF | - | IFI | - | -
Combustion gas main skid instrumentation junction box | - | r45.31-3323-TMT-ESR20-IJB01 | r45.31-3323-TMT-ESR20-IJB01-WC10 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR20-SKD01-PS0208 | Ignition gas high pressure switch SF | - | IFI | - | -
Combustion gas main skid instrumentation junction box | - | r45.31-3323-TMT-ESR20-IJB01 | r45.31-3323-TMT-ESR20-IJB01-WC11 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR20-SKD01-PS0209 | Ignition gas high pressure switch SF | - | IFI | - | -
Combustion gas main skid instrumentation junction box | - | r45.31-3323-TMT-ESR20-IJB01 | r45.31-3323-TMT-ESR20-IJB01-WP01 | CWP01 | 3G1,5 | 10 | RV-K 0,6/1kV | - | 3323-TMT-ESR20-SKD01-SV0201 | Main gas valve | - | IFI | - | -
Combustion gas main skid instrumentation junction box | - | r45.31-3323-TMT-ESR20-IJB01 | r45.31-3323-TMT-ESR20-IJB01-WP02 | CWP01 | 3G1,5 | 10 | RV-K 0,6/1kV | - | 3323-TMT-ESR20-SKD01-SV0202 | Ven gas valve | - | IFI | - | -
Combustion gas main skid instrumentation junction box | - | r45.31-3323-TMT-ESR20-IJB01 | r45.31-3323-TMT-ESR20-IJB01-WC12 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 5523-TMT-ESR40-SKD01-SZ0401 | Controlled descent valve limit switch | - | IFI | - | -
Compressed air main skid instrumentation junction box | - | r45.31-3323-TMT-ESR50-IJB01 | r45.31-3323-TMT-ESR50-IJB01-WC01 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR50-SKD01-SV0501A | Solenoid valve + limit switch | - | IFI | - | -
Compressed air main skid instrumentation junction box | - | r45.31-3323-TMT-ESR50-IJB01 | r45.31-3323-TMT-ESR50-IJB01-WC02 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR50-SKD01-SV0501A | Solenoid valve + limit switch | - | IFI | - | -
Compressed air main skid instrumentation junction box | - | r45.31-3323-TMT-ESR50-IJB01 | r45.31-3323-TMT-ESR50-IJB01-WC03 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR50-SKD01-SV0501B | Solenoid valve + limit switch | - | IFI | - | -
Compressed air main skid instrumentation junction box | - | r45.31-3323-TMT-ESR50-IJB01 | r45.31-3323-TMT-ESR50-IJB01-WC04 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR50-SKD01-SV0501B | Solenoid valve + limit switch | - | IFI | - | -
Compressed air main skid instrumentation junction box | - | r45.31-3323-TMT-ESR50-IJB01 | r45.31-3323-TMT-ESR50-IJB01-WC05 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR50-SKD01-PS0501 | Main compressed air low pressure switch | - | IFI | - | -
Compressed air main skid instrumentation junction box | - | r45.31-3323-TMT-ESR50-IJB01 | r45.31-3323-TMT-ESR50-IJB01-WC06 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-ESR50-SKD03-PS0501 | Air cannon compressed air low pressure switch | - | IFI | - | -
Compressed air main skid instrumentation junction box | - | r45.31-3323-TMT-ESR50-IJB01 | r45.31-3323-TMT-ESR50-IJB01-WC07 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-PNS03-ACN01-SV1501 | Solenoid valve + limit switch | - | IFI | - | -
Compressed air main skid instrumentation junction box | - | r45.31-3323-TMT-ESR50-IJB01 | r45.31-3323-TMT-ESR50-IJB01-WC08 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-PNS03-ACN01-SV1501 | Solenoid valve + limit switch | - | IFI | - | -
Compressed air main skid instrumentation junction box | - | r45.31-3323-TMT-ESR50-IJB01 | r45.31-3323-TMT-ESR50-IJB01-WC09 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-PNS03-ACN02-SV1501 | Solenoid valve + limit switch | - | IFI | - | -
Compressed air main skid instrumentation junction box | - | r45.31-3323-TMT-ESR50-IJB01 | r45.31-3323-TMT-ESR50-IJB01-WC10 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-PNS03-ACN02-SV1501 | Solenoid valve + limit switch | - | IFI | - | -
Chimney instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB03 | r45.31-3323-TMT-MCH01-IJB03-WP01 | CWP01 | 3G1,5 | 10 | RV-K 0,6/1kV | - | 3323-TMT-MCH01-HOO01-MV1101 | Servomotor | - | IFI | - | -
Chimney instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB03 | r45.31-3323-TMT-MCH01-IJB03-WC01 | CWC01 | 7G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-HOO01-MV1101 | Servomotor | - | IFI | - | -
Chimney instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB03 | r45.31-3323-TMT-MCH01-IJB03-WC02 | CWC02 | 5G1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-MCH01-HOO01-MV1101 | Servomotor | - | IFI | - | -
Chimney instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB03 | r45.31-3323-TMT-MCH01-IJB03-WP02 | CWP01 | 3G1,5 | 10 | RV-K 0,6/1kV | - | 3323-TMT-MCH01-CHY01-MV1101 | Servomotor | - | IFI | - | -
Chimney instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB03 | r45.31-3323-TMT-MCH01-IJB03-WC03 | CWC01 | 7G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-CHY01-MV1101 | Servomotor | - | IFI | - | -
Chimney instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB03 | r45.31-3323-TMT-MCH01-IJB03-WC04 | CWC02 | 5G1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-MCH01-CHY01-MV1101 | Servomotor | - | IFI | - | -
Chimney instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB03 | r45.31-3323-TMT-MCH01-IJB03-WC05 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-CHY01-ZS1101 | Chimney damper open limit switch SF | - | IFI | - | -
Chimney instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB03 | r45.31-3323-TMT-MCH01-IJB03-WC07 | CWC02 | 4G1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-MCH01-CHY01-SV1101 | Chimney damper control valve | - | IFI | - | -
Chimney instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB03 | r45.31-3323-TMT-MCH01-IJB03-WC10 | CWC02 | 3G1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-ACS02-GEN01-FCV1701 | Air curtain actuator | - | IFI | - | -
Chimney instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB03 | r45.31-3323-TMT-MCH01-IJB03-WP03 | CWP01 | 3G1,5 | 10 | RV-K 0,6/1kV | - | 3323-TMT-MCH01-CHY01-PT1101 | Furnace exhaust pressure | - | IFI | - | -
Chimney instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB03 | r45.31-3323-TMT-MCH01-IJB03-WC11 | CWC01 | 3x1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-CHY01-PT1101 | Furnace exhaust pressure | - | IFI | - | -
Chimney instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB03 | r45.31-3323-TMT-MCH01-IJB03-WC12 | CWC02 | 2x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-MCH01-CHY01-PT1101 | Furnace exhaust pressure | - | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WE01 | CWE02 | SF/UTP | 5 | 6XV1840-2AH10 | - | r45.31-3323-TMT-MCH01-RIO01 | - | Auxiliaries remote IO | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC01 | CWC03 | TC K | 10 | SIL-FV-MM | - | 3323-TMT-CBS01-BRN01-TE1201 | Burner #01 exhaust air temperature | - | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC02 | CWC03 | TC K | 10 | SIL-FV-MM | - | 3323-TMT-CBS01-BRN02-TE1201 | Burner #02 exhaust air temperature | - | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC03 | CWC02 | 3G1+SH | 11 | RC4V-K 300/500V | - | r45.31-3323-TMT-CBS01-IJB04 | - | O2 instrumentation junction box | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC04 | CWC02 | 3G1+SH | 11 | RC4V-K 300/500V | - | r45.31-3323-TMT-CBS01-IJB04 | - | O2 instrumentation junction box | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC05 | CWC02 | 4x1+SH | 11 | RC4V-K 300/500V | - | r45.31-3323-TMT-CBS01-IJB04 | - | O2 instrumentation junction box | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC06 | CWC02 | 3G1+SH | 11 | RC4V-K 300/500V | - | r45.31-3323-TMT-CBS01-IJB05 | - | O2 instrumentation junction box | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC07 | CWC02 | 3G1+SH | 11 | RC4V-K 300/500V | - | r45.31-3323-TMT-CBS01-IJB05 | - | O2 instrumentation junction box | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC08 | CWC02 | 4x1+SH | 11 | RC4V-K 300/500V | - | r45.31-3323-TMT-CBS01-IJB05 | - | O2 instrumentation junction box | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC15 | CWC01 | 24G1 | 10 | YSLY 300/500V | - | r45.31-3323-TMT-CBS01-IJB01 | - | Burners roof area instrumentation junction box | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC16 | CWC02 | 24G1+SH | 10 | RC4V-K 300/500V | - | r45.31-3323-TMT-CBS01-IJB01 | - | Burners roof area instrumentation junction box | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC17 | CWC02 | 24G1+SH | 10 | RC4V-K 300/500V | - | r45.31-3323-TMT-CBS01-IJB01 | - | Burners roof area instrumentation junction box | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC18 | CWC01 | 24G1 | 10 | YSLY 300/500V | - | r45.31-3323-TMT-CBS01-IJB01 | - | Burners roof area instrumentation junction box | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC19 | CWC02 | 24G1+SH | 10 | RC4V-K 300/500V | - | r45.31-3323-TMT-CBS01-IJB01 | - | Burners roof area instrumentation junction box | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC20 | CWC02 | 24G1+SH | 10 | RC4V-K 300/500V | - | r45.31-3323-TMT-CBS01-IJB01 | - | Burners roof area instrumentation junction box | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC21 | CWC01 | 16G1 | 16 | YSLY 300/500V | - | r45.31-3323-TMT-CBS01-IJB02 | - | Burner #1 instrumentation junction box | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WP01 | CWP01 | 4G1,5 | 14 | RV-K 0,6/1kV | - | r45.31-3323-TMT-CBS01-BCU01 | - | Burner Control Unit #01 | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WE02 | CWE02 | SF/UTP | 14 | 6XV1840-2AH10 | - | r45.31-3323-TMT-CBS01-BCU01 | - | Burner Control Unit #01 | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC22 | CWC01 | 7G1 | 14 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN01-TTC1201 | Burner#01 leak test unit | - | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC23 | CWC01 | 16G1 | 13 | YSLY 300/500V | - | r45.31-3323-TMT-CBS01-IJB03 | - | Burner #2 instrumentation junction box | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WP02 | CWP01 | 4G1,5 | 12 | RV-K 0,6/1kV | - | r45.31-3323-TMT-CBS01-BCU02 | - | Burner Control Unit #02 | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WE03 | CWE02 | SF/UTP | 12 | 6XV1840-2AH10 | - | r45.31-3323-TMT-CBS01-BCU02 | - | Burner Control Unit #02 | IFI | - | -
Combustion area remote IO | - | r45.31-3323-TMT-CBS01-RIO01 | r45.31-3323-TMT-CBS01-RIO01-WC24 | CWC01 | 7G1 | 13 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN02-TTC1201 | Burner#02 leak test unit | - | IFI | - | -
O2 instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB04 | r45.31-3323-TMT-CBS01-IJB04-WC01 | Probe cable FEP-0001 | Probe cable FEP-0001 | - | - | - | 3323-TMT-CBS01-GEN01-AE1201 | Exhaust air oxygen prove | - | IFI | - | -
O2 instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB05 | r45.31-3323-TMT-CBS01-IJB05-WC01 | Probe cable FEP-0001 | Probe cable FEP-0001 | - | - | - | 3323-TMT-CBS01-GEN01-AE1202 | Exhaust air oxygen prove | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC01 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-TE1203 | Combustion air temperature transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC02 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-TE1204 | Combustion air temperature transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC03 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-PT1203 | Combustion air pressure transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC04 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-PT1204 | Combustion air pressure transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC05 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-PDT1202 | Combustion air flow transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC06 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-PDT1203 | Combustion air flow transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC07 | CWC02 | 5G1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-FCV1202 | 2nd stage air flow control valve | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC08 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN01-SV1204 | Solenoid valve + limit switch | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC09 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN01-SV1204 | Solenoid valve + limit switch | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC10 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN02-SV1204 | Solenoid valve + limit switch | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC11 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN02-SV1204 | Solenoid valve + limit switch | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC12 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-PDT1204 | 1st stage air flow transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC13 | CWC02 | 5G1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-FCV1203 | 1st stage air flow control valve | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC15 | CWC01 | 3x1 | 10 | YSLY 300/500V | - | 3323-TMT-CBS01-GEN01-PS1201 | Main combustion gas pressure switch SF | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC16 | CWC01 | 3x1 | 10 | YSLY 300/500V | - | 3323-TMT-CBS01-GEN01-PS1202 | Ignition gas pressure switch SF | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC17 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-TE1201 | Combustion gas temperature transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC18 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-TE1202 | Combustion gas temperature transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC19 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-PT1201 | Combustion gas pressure transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC20 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-PT1202 | Combustion gas pressure transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC21 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-PDT1200 | Combustion gas flow transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC22 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-PDT1201 | Combustion gas flow transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC23 | CWC02 | 5G1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-FCV1201 | Main gas flow control valve | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC25 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-PDT1205 | Exhaust air flow transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC26 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-PT1205 | Exhaust air pressure transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC27 | CWC02 | 5G1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-GEN01-FCV1204 | Exhaust air flow control valve | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC28 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN01-SV1205 | Solenoid valve + limit switch | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC29 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN01-SV1205 | Solenoid valve + limit switch | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC30 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN02-SV1205 | Solenoid valve + limit switch | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC31 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN02-SV1205 | Solenoid valve + limit switch | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC32 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-BRN01-PDT1201 | Burner #01 media case flow transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC33 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-CBS01-BRN02-PDT1201 | Burner #02 media case flow transmitter | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC35 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-PNS01-GEN01-PS1501 | Combustion compressed air low pressure switch SF | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC40 | CWC01 | 3x1 | 10 | YSLY 300/500V | - | 3323-TMT-ACS01-GEN01-PDT1701 | O2 lance cooling air low flow switch SF | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC41 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-OXS01-GEN01-FCV1301 | O2 lance cooling flow control valve + limit switch | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC42 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-OXS01-GEN01-FCV1301 | O2 lance cooling flow control valve + limit switch | - | IFI | - | -
Burners roof area instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB01 | r45.31-3323-TMT-CBS01-IJB01-WC43 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-PNS02-GEN01-SV1501 | O2 lance pilot air solenoid valve | - | IFI | - | -
Burner #1 instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB02 | r45.31-3323-TMT-CBS01-IJB02-WC01 | CWC01 | 3x1 | 10 | YSLY 300/500V | - | 3323-TMT-ACS01-BRN01-PS1701 | Burner#01 cooling air low pressure switch | - | IFI | - | -
Burner #1 instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB02 | r45.31-3323-TMT-CBS01-IJB02-WC02 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN01-FCV1203 | Burner#01 1st stage air flow control valve | - | IFI | - | -
Burner #1 instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB02 | r45.31-3323-TMT-CBS01-IJB02-WC03 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN01-FCV1203 | Burner#01 1st stage air flow control valve | - | IFI | - | -
Burner #1 instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB02 | r45.31-3323-TMT-CBS01-IJB02-WC04 | CWC01 | 5G0,5 | 10 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN01-SV1201/SV1202 | Burner#01 Main gas SSOV feedback | - | IFI | - | -
Burner Control Unit #01 | - | r45.31-3323-TMT-CBS01-BCU01 | r45.31-3323-TMT-CBS01-BCU01-WC01 | CWC06 | 1x6 | 8 | OLFLEX HEAT 180SiF | - | 3323-TMT-CBS01-BRN01-BR1202 | Burner#01 pilot burner | - | IFI | - | -
Burner Control Unit #01 | - | r45.31-3323-TMT-CBS01-BCU01 | r45.31-3323-TMT-CBS01-BCU01-WC02 | CWC05 | 1x1 | 8 | OLFLEX HEAT 180 FZLSi | - | 3323-TMT-CBS01-BRN01-BR1202 | Burner#01 pilot burner | - | IFI | - | -
Burner Control Unit #01 | - | r45.31-3323-TMT-CBS01-BCU01 | r45.31-3323-TMT-CBS01-BCU01-WC03 | CWC01 | 4G0,5 | 8 | OLFLEX HEAT 180 C MS | - | 3323-TMT-CBS01-BRN01-BE1201 | 3323-TMT-CBS01-BRN01-BE1201 | - | IFI | - | -
Burner Control Unit #01 | - | r45.31-3323-TMT-CBS01-BCU01 | r45.31-3323-TMT-CBS01-BCU01-WP01 | CWP04 | 3G0,5 | 8 | OLFLEX HEAT 180 C MS | - | 3323-TMT-CBS01-BRN01-SV1203 | 3323-TMT-CBS01-BRN01-SV1203 | - | IFI | - | -
Burner Control Unit #01 | - | r45.31-3323-TMT-CBS01-BCU01 | r45.31-3323-TMT-CBS01-BCU01-WP02 | CWP04 | 3G0,5 | 8 | OLFLEX HEAT 180 C MS | - | 3323-TMT-CBS01-BRN01-SV1204 | 3323-TMT-CBS01-BRN01-SV1204 | - | IFI | - | -
Burner Control Unit #01 | - | r45.31-3323-TMT-CBS01-BCU01 | r45.31-3323-TMT-CBS01-BCU01-WP03 | CWP04 | 3G0,5 | 8 | OLFLEX HEAT 180 C MS | - | 3323-TMT-CBS01-BRN01-SV1201/SV1202 | Burner#01 Main gas SSOV | - | IFI | - | -
Burner #2 instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB03 | r45.31-3323-TMT-CBS01-IJB03-WC01 | CWC01 | 3x1 | 8 | YSLY 300/500V | - | 3323-TMT-ACS01-BRN02-PS1701 | Burner#02 cooling air low pressure switch (440) | - | IFI | - | -
Burner #2 instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB03 | r45.31-3323-TMT-CBS01-IJB03-WC02 | CWC01 | 3G1 | 8 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN02-FCV1203 | Burner#02 1st stage air flow control valve (490) | - | IFI | - | -
Burner #2 instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB03 | r45.31-3323-TMT-CBS01-IJB03-WC03 | CWC01 | 4G1 | 8 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN02-FCV1203 | Burner#02 1st stage air flow control valve (490) | - | IFI | - | -
Burner #2 instrumentation junction box | - | r45.31-3323-TMT-CBS01-IJB03 | r45.31-3323-TMT-CBS01-IJB03-WC04 | CWC01 | 5G0,5 | 8 | YSLY 300/500V | - | 3323-TMT-CBS01-BRN02-SV1201/SV1202 | Burner#02 Main gas SSOV feedback (900-910) | - | IFI | - | -
Burner Control Unit #02 | - | r45.31-3323-TMT-CBS01-BCU02 | r45.31-3323-TMT-CBS01-BCU02-WC01 | CWC06 | 1x6 | 8 | OLFLEX HEAT 180SiF | - | 3323-TMT-CBS01-BRN02-BR1202 | Burner#02 pilot burner (20) | - | IFI | - | -
Burner Control Unit #02 | - | r45.31-3323-TMT-CBS01-BCU02 | r45.31-3323-TMT-CBS01-BCU02-WC02 | CWC05 | 1x1 | 8 | OLFLEX HEAT 180 FZLSi | - | 3323-TMT-CBS01-BRN02-BR1202 | Burner#02 pilot burner (20) | - | IFI | - | -
Burner Control Unit #02 | - | r45.31-3323-TMT-CBS01-BCU02 | r45.31-3323-TMT-CBS01-BCU02-WC03 | CWC01 | 4G0,5 | 8 | OLFLEX HEAT 180 C MS | - | 3323-TMT-CBS01-BRN02-BE1201 | Burner#02 UV Sensor (230) | - | IFI | - | -
Burner Control Unit #02 | - | r45.31-3323-TMT-CBS01-BCU02 | r45.31-3323-TMT-CBS01-BCU02-WP01 | CWP04 | 3G0,5 | 8 | OLFLEX HEAT 180 C MS | - | 3323-TMT-CBS01-BRN02-SV1203 | Burner#02 Pilot gas SSOV (100) | - | IFI | - | -
Burner Control Unit #02 | - | r45.31-3323-TMT-CBS01-BCU02 | r45.31-3323-TMT-CBS01-BCU02-WP02 | CWP04 | 3G0,5 | 8 | OLFLEX HEAT 180 C MS | - | 3323-TMT-CBS01-BRN02-SV1204 | Burner#02 Pilot gas SSOV (100) | - | IFI | - | -
Burner Control Unit #02 | - | r45.31-3323-TMT-CBS01-BCU02 | r45.31-3323-TMT-CBS01-BCU02-WP03 | CWP04 | 3G0,5 | 8 | OLFLEX HEAT 180 C MS | - | 3323-TMT-CBS01-BRN02-SV1201/SV1202 | Burner#02 Main gas SSOV (900-910) | - | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WE01 | CWE02 | SF/UTP | 23 | 6XV1840-2AH10 | - | r45.31-3323-TMT-GEN01-PDP01 |  | Plant cable routing power distribution panel | IFI | - | -
Plant cable routing power distribution panel | - | r45.31-3323-TMT-GEN01-PDP01 | r45.31-3323-TMT-GEN01-PDP01-WE02 | CWE02 | SF/UTP | 107 | 6XV1840-2AH10 | - | r4z.41-3323-THD-GEN01-PCP01 |  | THD main power control panel | AIB | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC01 | CWC02 | 3x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-MCH01-GEN01-PT1101 | Furnace pressure transmitter | - | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC02 | CWC03 | TC K | 10 | SIL-FV-MM | - | 3323-TMT-MCH01-GEN01-TE1103 | Furnace roof temperature | - | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC03 | CWC03 | TC K | 10 | SIL-FV-MM | - | 3323-TMT-MCH01-GEN01-TE1101A | Furnace roof safety temp | - | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC04 | CWC03 | TC K | 10 | SIL-FV-MM | - | 3323-TMT-MCH01-GEN01-TE1101B | Furnace roof safety temp. | - | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC05 | CWC03 | TC K | 10 | SIL-FV-MM | - | 3323-TMT-MCH01-TEX01-TE1102 | Furnace bath temperature | - | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC06 | CWC02 | 4x1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-MCH01-GEN01-ZT1101 | Furnace tilting angle | - | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC07 | CWC02 | 3G1+SH | 10 | RC4V-K 300/500V | - | 3323-TMT-MCH01-MLM01-LT1101 | Furnace bath level | - | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC08 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-MLM01-PS1101 | Furnace level sensor cooling compressed air low pressure switch | - | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC09 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-CTV01-CAM01-PS1101 | Fioscope camera #01 compressed air low pressure switch SF | - | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC10 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-CTV01-CAM02-PS1101 | Fioscope camera #02 compressed air low pressure switch SF | - | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC11 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-GEN01-ZSxxx | Tilting down limit switch SF | - | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC15 | CWC01 | 18G1 | 20 | YSLY 300/500V | - | r45.31-3323-TMT-MCH01-LCB01 | - | Roof access local control box | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC16 | CWC01 | 16G1 | 15 | YSLY 300/500V | - | r45.31-3323-TMT-MCH01-LCB02 | - | Main door local control box | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC17 | CWC01 | 18G1 | 15 | YSLY 300/500V | - | r45.31-3323-TMT-MCH01-LCB03 | - | Bath TC local control box | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC18 | CWC01 | 16G1 | 20 | YSLY 300/500V | - | r45.31-3323-TMT-MCH01-LCB04 | - | Side door local control box | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC19 | CWC01 | 12G1 | 12 | YSLY 300/500V | - | r45.31-3323-TMT-MCH01-IJB01 | - | Left side door instrumentation junction box | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC20 | CWC01 | 12G1 | 15 | YSLY 300/500V | - | r45.31-3323-TMT-MCH01-IJB02 | - | Right side door instrumentation junction box | IFI | - | -
Auxiliaries remote IO | - | r45.31-3323-TMT-MCH01-RIO01 | r45.31-3323-TMT-MCH01-RIO01-WC21 | CWC01 | 12G1 | 22 | YSLY 300/500V | - | r45.31-3323-TMT-MCH01-IJB04 | - | Spout cover instrumentation junction box | IFI | - | -
Roof access local control box | - | r45.31-3323-TMT-MCH01-LCB01 | r45.31-3323-TMT-MCH01-LCB01-WC01 | CWC01 | 12G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-GEN01-XRA1101 | Furnace roof safety registry access | - | IFI | - | -
Bath TC local control box | - | r45.31-3323-TMT-MCH01-LCB03 | r45.31-3323-TMT-MCH01-LCB03-WC02 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-TEX01-ZS1101A | Limit switch inserted position A | - | IFI | - | -
Bath TC local control box | - | r45.31-3323-TMT-MCH01-LCB03 | r45.31-3323-TMT-MCH01-LCB03-WC03 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-TEX01-ZS1101B | Limit switch inserted position B | - | IFI | - | -
Bath TC local control box | - | r45.31-3323-TMT-MCH01-LCB03 | r45.31-3323-TMT-MCH01-LCB03-WC04 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-TEX01-ZS1101C | Limit switch inserted position C | - | IFI | - | -
Side door local control box | - | r45.31-3323-TMT-MCH01-LCB04 | r45.31-3323-TMT-MCH01-LCB04-WC01 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-GAT01-ZS1101 | Furnace side door open limit switch SF | - | IFI | - | -
Side door local control box | - | r45.31-3323-TMT-MCH01-LCB04 | r45.31-3323-TMT-MCH01-LCB04-WC02 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-GAT01-ZS1102 | Furnace side door closed limit switch SF | - | IFI | - | -
Left side door instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB01 | r45.31-3323-TMT-MCH01-IJB01-WC01 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-DOO01-ZS1101 | Main door left side loose switch | - | IFI | - | -
Left side door instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB01 | r45.31-3323-TMT-MCH01-IJB01-WC02 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-DOO01-ZS1102 | Main door left side tighting switch SF | - | IFI | - | -
Left side door instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB01 | r45.31-3323-TMT-MCH01-IJB01-WC03 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-DOO01-ZS1105 | Main door opened switch SF | - | IFI | - | -
Left side door instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB01 | r45.31-3323-TMT-MCH01-IJB01-WC04 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-DOO01-ZS1106 | Main door closed switch SF | - | IFI | - | -
Right side door instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB02 | r45.31-3323-TMT-MCH01-IJB02-WC01 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-DOO01-ZS1103 | Main door right side loose switch SF | - | IFI | - | -
Right side door instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB02 | r45.31-3323-TMT-MCH01-IJB02-WC02 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-DOO01-ZS1104 | Main door right side tighting switch SF | - | IFI | - | -
Spout cover instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB04 | r45.31-3323-TMT-MCH01-IJB04-WC01 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-TTS01-ZS1101 | Spout cover open position switch SF | - | IFI | - | -
Spout cover instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB04 | r45.31-3323-TMT-MCH01-IJB04-WC02 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-TTS01-ZS1102 | Spout cover open position switch SF | - | IFI | - | -
Spout cover instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB04 | r45.31-3323-TMT-MCH01-IJB04-WC03 | CWC01 | 3G1,5 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-TTS01-LS1101 | Spout cover level switch SF | - | IFI | - | -
Spout cover instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB04 | r45.31-3323-TMT-MCH01-IJB04-WC04 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-TTS01-SV1101A | Solenoid valve | - | IFI | - | -
Spout cover instrumentation junction box | - | r45.31-3323-TMT-MCH01-IJB04 | r45.31-3323-TMT-MCH01-IJB04-WC05 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-MCH01-TTS01-SV1101B | Solenoid valve | - | IFI | - | -
Monitoring camera power control panel #01 | - | r45.31-3323-TMT-CVT01-PCP01 | r45.31-3323-TMT-CVT01-PCP01-WE01 | CWE02 | SF/UTP | 24 | 6XV1840-2AH10 | - | r45.31-3323-TMT-GEN01-PDP01 | - | Plant cable routing power distribution panel | IFI | - | -
Strip cast back area communication junction box | - | r41.31-0600-GEN-CVT01-CJB03 | r41.31-0600-GEN-CTV01-CJB03-WE17 | CWE02 | SF/UTP | 26 | 6XV1840-2AH10 | - | r45.31-3323-TMT-GEN01-PDP01 | - | Plant cable routing power distribution panel | IFI | - | -
Monitoring camera power control panel #01 | - | r45.31-3323-TMT-CVT01-PCP01 | r45.31-3323-TMT-CVT01-PCP01-WE02 | CWE02 | SF/UTP | 8 | 6XV1840-2AH10 | - | r45.31-3323-TMT-MCH01-RIO01 | - | Auxiliaries remote IO | IFI | - | -
Monitoring camera power control panel #01 | - | r45.31-3323-TMT-CVT01-PCP01 | r45.31-3323-TMT-CVT01-PCP01-WC01 | CWC01 | 2x1 | 8 | YSLY 300/500V | - | r45.31-3323-TMT-MCH01-RIO01 | - | Auxiliaries remote IO | IFI | - | -
Monitoring camera power control panel #01 | - | r45.31-3323-TMT-CVT01-PCP01 | r45.31-3323-TMT-CVT01-PCP01-WP01 | CWP01 | 4G4 | 10 | RV-K 0,6/1kV | - | 3323-CVT01-GEN-ACF01-M01 | BLOWER | - | IFI | - | -
Monitoring camera power control panel #01 | - | r45.31-3323-TMT-CVT01-PCP01 | r45.31-3323-TMT-CVT01-PCP01-WC02 | CWC01 | 16G1 | 6 | YSLY 300/500V | - | r45.31-3323-TMT-CVT01-LCB01 | - | Monitoring camera local control box #01 | IFI | - | -
Monitoring camera power control panel #01 | - | r45.31-3323-TMT-CVT01-PCP01 | r45.31-3323-TMT-CVT01-PCP01-WC03 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-CVT01-CAM01-SDIxxxx | Propietary camera head cable | - | IFI | - | -
Monitoring camera power control panel #01 | - | r45.31-3323-TMT-CVT01-PCP01 | r45.31-3323-TMT-CVT01-PCP01-WC04 | CWC03 | TC K | 10 | SIL-FV-MM | - | 3323-TMT-CVT01-CAM01-TExxxx | TC-cable | - | IFI | - | -
Monitoring camera local control box #01 | - | r45.31-3323-TMT-CVT01-LCB01 | r45.31-3323-TMT-CVT01-LCB01-WC01 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-CVT01-CAM01-SVxxxx | Solenoid valve | - | IFI | - | -
Monitoring camera local control box #01 | - | r45.31-3323-TMT-CVT01-LCB01 | r45.31-3323-TMT-CVT01-LCB01-WC02 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-CVT01-CAM01-ZSxxxx | Limit switch | - | IFI | - | -
Monitoring camera local control box #01 | - | r45.31-3323-TMT-CVT01-LCB01 | r45.31-3323-TMT-CVT01-LCB01-WC03 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-CVT01-CAM01-ZSxxxx | Limit switch | - | IFI | - | -
Monitoring camera power control panel #02 | - | r45.31-3323-TMT-CVT01-PCP02 | r45.31-3323-TMT-CVT01-PCP02-WE01 | CWE02 | SF/UTP | 24 | 6XV1840-2AH10 | - | r45.31-3323-TMT-GEN01-PDP01 | - | Plant cable routing power distribution panel | IFI | - | -
Strip cast back area communication junction box | - | r41.31-0600-GEN-CVT01-CJB03 | r41.31-0600-GEN-CTV01-CJB03-WE18 | CWE02 | SF/UTP | 26 | 6XV1840-2AH10 | - | r45.31-3323-TMT-GEN01-PDP01 | - | Plant cable routing power distribution panel | IFI | - | -
Monitoring camera power control panel #02 | - | r45.31-3323-TMT-CVT01-PCP02 | r45.31-3323-TMT-CVT01-PCP02-WE02 | CWE02 | SF/UTP | 5 | 6XV1840-2AH10 | - | r45.31-3323-TMT-MCH01-RIO01 | - | Auxiliaries remote IO | IFI | - | -
Monitoring camera power control panel #02 | - | r45.31-3323-TMT-CVT01-PCP02 | r45.31-3323-TMT-CVT01-PCP02-WC01 | CWC01 | 2x1 | 5 | YSLY 300/500V | - | r45.31-3323-TMT-MCH01-RIO01 | - | Auxiliaries remote IO | IFI | - | -
Monitoring camera power control panel #02 | - | r45.31-3323-TMT-CVT01-PCP02 | r45.31-3323-TMT-CVT01-PCP02-WP01 | CWP01 | 4G4 | 10 | RV-K 0,6/1kV | - | 3323-TMT-CVT01-ACF02-M01 | BLOWER | - | IFI | - | -
Monitoring camera power control panel #02 | - | r45.31-3323-TMT-CVT01-PCP02 | r45.31-3323-TMT-CVT01-PCP02-WC02 | CWC01 | 16G1 | 8 | YSLY 300/500V | - | r45.31-3323-TMT-CVT01-LCB02 | - | Monitoring camera local control box #02 | IFI | - | -
Monitoring camera power control panel #02 | - | r45.31-3323-TMT-CVT01-PCP02 | r45.31-3323-TMT-CVT01-PCP02-WC03 | CWC01 | 4G1 | 10 | YSLY 300/500V | - | 3323-TMT-CVT01-CAM01-SDIxxxx | Propietary camera head cable | - | IFI | - | -
Monitoring camera power control panel #02 | - | r45.31-3323-TMT-CVT01-PCP02 | r45.31-3323-TMT-CVT01-PCP02-WC04 | CWC03 | TC K | 10 | SIL-FV-MM | - | 3323-TMT-CVT01-CAM01-TExxxx | TC-cable | - | IFI | - | -
Monitoring camera local control box #02 | - | r45.31-3323-TMT-CVT01-LCB02 | r45.31-3323-TMT-CVT01-LCB02-WC01 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-CVT01-CAM02-SVxxxx | Solenoid valve | - | IFI | - | -
Monitoring camera local control box #02 | - | r45.31-3323-TMT-CVT01-LCB02 | r45.31-3323-TMT-CVT01-LCB02-WC02 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-CVT01-CAM02-ZSxxxx | Limit switch | - | IFI | - | -
Monitoring camera local control box #02 | - | r45.31-3323-TMT-CVT01-LCB02 | r45.31-3323-TMT-CVT01-LCB02-WC03 | CWC01 | 3G1 | 10 | YSLY 300/500V | - | 3323-TMT-CVT01-CAM02-ZSxxxx | Limit switch | - | IFI | - | -