## Cover
Client: |  | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
Cover
CUSTOMER: |  | ALINVEST | PREPARED: | JOBI
PROJECT CODE: |  | E2558 | REVIEWED: | ANSA
PROJECT NAME: |  | ALFAGEN | DATE: | 2025/12/04
CONTRACTOR DOC. CODE: |  | 2558-5521-GEN-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: |  | 2558-5521-GEN-E-LST-CBLS | PAGE: | 01 of 05
REVISION CONTROL
REV | DATE | DESCRIPTON |  | PAGE
A | 2025/12/01 | Issue for information |  | 1-5
B
C
D
E
F
G
H
I
J
K
L
M
N
O
P
Q
R
S
T
U
V
W
X
Y
Z
AA
AB
AC
AD
AE
The drawing(s), document(s) and the information contained herein are the property of INDUSTRIAL FURNACES INSERTEC. And they shall not be disclosed, reproduced or used in any manner without the prior written consent of INDUSTRIAL FURNACES INSERTEC. Offenders will be held liable for the payment of damages.

## Table of Contents
Client: |  | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
Table of contents
CUSTOMER: |  | ALINVEST | PREPARED: | JOBI
PROJECT CODE: |  | E2558 | REVIEWED: | ANSA
PROJECT NAME: |  | ALFAGEN | DATE: | 2025/12/04
CONTRACTOR DOC. CODE: |  | 2558-5521-GEN-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: |  | 2558-5521-GEN-E-LST-CBLS | PAGE: | 02 of 05
Table of contents
SEC | DESCRIPTON |  |  | PAGE
0 | Cover |  |  | 1
1 | Table of contents |  |  | 2
2 | Definitions |  |  | 3
3 | Equipment cable list |  |  | 4-5
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
The drawing(s), document(s) and the information contained herein are the property of INDUSTRIAL FURNACES INSERTEC. And they shall not be disclosed, reproduced or used in any manner without the prior written consent of INDUSTRIAL FURNACES INSERTEC. Offenders will be held liable for the payment of damages.

## Definitions
Client: | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
DEFINITIONS
CUSTOMER: | ALINVEST | PREPARED: | JOBI
PROJECT CODE: | E2558 | REVIEWED: | ANSA
PROJECT NAME: | ALFAGEN | DATE: | 2025/12/04
CONTRACTOR DOC. CODE: | 2558-5521-GEN-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: | 2558-5521-GEN-E-LST-CBLS | PAGE: | 03 of 05
MAIN DEFINITIONS
== -
= -
++ -
+ -
Description -
IME (Complete) -
Tag - For more detail, please refer to B001-B002-GEN-E-PRC-NPOS-R09 Numbering procedure for electrical objects and signals document.
Category - For more detail, please refer to B001-B002-GNL-E-SPC-INCC-R02 Technical specification for cables and cable trays document.
Type - Cable type according to conductor number, section, shield, etc
Length - Estimated lenght of the given cable.
Page - Page number realted to the electrical schematics. Refer to: B001-B002-B003-E-DWG-ESCH-R00 Equipment electrical schematics
Function -
Remarks - Notes to be considered.
Revision change comments - Revision change reason comments.

## Equipment cable list
Client: | CUSTOMER: | ALINVEST |  | EQUIPMENT CABLE LIST | [7 empty] | PREPARED: | JOBI | Contractor:
ALINVEST | PROJECT CODE: | E2558 | [9 empty] | REVIEWED: | ANSA
| PROJECT NAME: | ALFAGEN | [9 empty] | DATE: | 2025/12/04
| CONTRACTOR DOC. CODE: | 2558-5521-GEN-E-LST-CBLS | [9 empty] | REVISION: | A
| CUSTOMER DOC. CODE: | 2558-5521-GEN-E-LST-CBLS | [9 empty] | PAGE: | 04/05 of 05
SOURCE |  |  | CABLE | [5 empty] | DESTINATION |  |  | OTHERS
Location Description | Instrument Description | Device Tag | Tag | Category | Type | Length [m] | Cable Reference | Route | Device Tag | Instrument Description | Location Description | Scope of Supply | Remarks | Revision Change Comment
T143.61 | - | r43.61 | WL43.61.R1 | CWP01 | 1x95 | TBD BY CLIENT | - | - | r43.61-5521-GEN-ESR40-PCP01 | - | - | AIB | - | -
T143.61 | - | r43.61 | WL43.61.S1 | CWP01 | 1x95 | TBD BY CLIENT | - | - | r43.61-5521-GEN-ESR40-PCP01 | - | - | AIB | - | -
T143.61 | - | r43.61 | WL43.61.T1 | CWP01 | 1x95 | TBD BY CLIENT | - | - | r43.61-5521-GEN-ESR40-PCP01 | - | - | AIB | - | -
T143.61 | - | r43.61 | WL43.61.P1 | CWP01 | 1x95 PE | TBD BY CLIENT | - | - | r43.61-5521-GEN-ESR40-PCP01 | - | - | AIB | - | -
T143.61 | - | r43.61 | WL43.61.L1 | CWP01 | 3G2,5 | TBD BY CLIENT | - | - | r43.61-5521-GEN-ESR40-PCP01 | - | - | AIB | - | -
T143.61 | - | r43.61 | WL43.61.R2 | CWP01 | 1x95 | TBD BY CLIENT | - | - | FUTURE LINE | - | - | AIB | - | -
T143.61 | - | r43.61 | WL43.61.S2 | CWP01 | 1x95 | TBD BY CLIENT | - | - | FUTURE LINE | - | - | AIB | - | -
T143.61 | - | r43.61 | WL43.61.T2 | CWP01 | 1x95 | TBD BY CLIENT | - | - | FUTURE LINE | - | - | AIB | - | -
T143.61 | - | r43.61 | WL43.61.P2 | CWP01 | 1x95 PE | TBD BY CLIENT | - | - | FUTURE LINE | - | - | AIB | - | -
T143.61 | - | r43.61 | WL43.61.L2 | CWP01 | 3G2,5 | TBD BY CLIENT | - | - | FUTURE LINE | - | - | AIB | - | -
Hydraulic main power control panel | - | r43.61-5521-GEN-ESR40-PCP01 | r43.61-5521-GEN-ESR40-PCP01-WP01 | CWP02 | 4G10+SH | 60 | RC4V-K 0,6/1kV | - | r43.61-5521-GEN-ESR40-DSS01 | - | Hydraulic pump motor #01 disconnector switch | AIB | - | -
Hydraulic main power control panel | - | r43.61-5521-GEN-ESR40-PCP01 | r43.61-5521-GEN-ESR40-PCP01-WP02 | CWP02 | 4G10+SH | 60 | RC4V-K 0,6/1kV | - | r43.61-5521-GEN-ESR40-DSS02 | - | Hydraulic pump motor #02 disconnector switch | AIB | - | -
Hydraulic main power control panel | - | r43.61-5521-GEN-ESR40-PCP01 | r43.61-5521-GEN-ESR40-PCP01-WP03 | CWP02 | 4G10+SH | 60 | RC4V-K 0,6/1kV | - | r43.61-5521-GEN-ESR40-DSS03 | - | Hydraulic pump motor #03 disconnector switch | AIB | - | -
Hydraulic main power control panel | - | r43.61-5521-GEN-ESR40-PCP01 | r43.61-5521-GEN-ESR40-PCP01-WP04 | CWP01 | 4G2,5 | 60 | RV-K 0,6/1kV | - | r43.61-5521-GEN-ESR40-DSS04 | - | Hydraulic cooling pump motor #01 disconnector switch | AIB | - | -
Hydraulic main power control panel | - | r43.61-5521-GEN-ESR40-PCP01 | r43.61-5521-GEN-ESR40-PCP01-WP05 | CWP01 | 4G2,5 | 60 | RV-K 0,6/1kV | - | r43.61-5521-GEN-ESR40-DSS05 | - | Hydraulic cooling pump motor #02 disconnector switch | AIB | - | -
Hydraulic main power control panel | - | r43.61-5521-GEN-ESR40-PCP01 | r43.61-5521-GEN-ESR40-PCP01-WP06 | CWP01 | 4G2,5 | 60 | RV-K 0,6/1kV | - | r43.61-5521-GEN-ESR40-DSS06 | - | Oil heater #01 disconnector switch | AIB | - | -
Hydraulic main power control panel | - | r43.61-5521-GEN-ESR40-PCP01 | r43.61-5521-GEN-ESR40-PCP01-WP07 | CWP01 | 3G2,5 | 63 | RV-K 0,6/1kV | - | r43.61-5521-GEN-ESR40-RIO01 | Hydraulic energy sources remote I/O: technical room | - | AIB | - | -
Hydraulic main power control panel | - | r43.61-5521-GEN-ESR40-PCP01 | r43.61-5521-GEN-ESR40-PCP01-WP08 | CWP01 | 3G2,5 | 63 | RV-K 0,6/1kV | - | r43.61-5521-GEN-ESR40-RIO01 | Hydraulic energy sources remote I/O: technical room | - | AIB | - | -
Hydraulic main power control panel | - | r43.61-5521-GEN-ESR40-PCP01 | r43.61-5521-GEN-ESR40-PCP01-WE02 | CWE02 | SF/UTP | 63 | 6XV1840-2AH10 | - | r43.61-5521-GEN-ESR40-RIO01 | Hydraulic energy sources remote I/O: technical room | - | AIB | - | -
Hydraulic energy sources remote I/O: technical room | - | r43.61-5521-GEN-ESR40-RIO01 | r43.61-5521-GEN-ESR40-RIO01-WC01 | CWC01 | 2x1 | 10 | YSLY 300/500V | - | r43.61-5521-GEN-ESR40-DSS01 | - | Hydraulic pump motor #01 disconnector switch | IFI | - | -
Hydraulic energy sources remote I/O: technical room | - | r43.61-5521-GEN-ESR40-RIO01 | r43.61-5521-GEN-ESR40-RIO01-WC02 | CWC01 | 2x1 | 10 | YSLY 300/500V | - | r43.61-5521-GEN-ESR40-DSS02 | - | Hydraulic pump motor #02 disconnector switch | IFI | - | -
Hydraulic energy sources remote I/O: technical room | - | r43.61-5521-GEN-ESR40-RIO01 | r43.61-5521-GEN-ESR40-RIO01-WC03 | CWC01 | 2x1 | 10 | YSLY 300/500V | - | r43.61-5521-GEN-ESR40-DSS03 | - | Hydraulic pump motor #03 disconnector switch | IFI | - | -
Hydraulic energy sources remote I/O: technical room | - | r43.61-5521-GEN-ESR40-RIO01 | r43.61-5521-GEN-ESR40-RIO01-WC04 | CWC01 | 2x1 | 10 | YSLY 300/500V | - | r43.61-5521-GEN-ESR40-DSS04 | - | Hydraulic cooling pump motor #01 disconnector switch | IFI | - | -
Hydraulic energy sources remote I/O: technical room | - | r43.61-5521-GEN-ESR40-RIO01 | r43.61-5521-GEN-ESR40-RIO01-WC05 | CWC01 | 2x1 | 10 | YSLY 300/500V | - | r43.61-5521-GEN-ESR40-DSS05 | - | Hydraulic cooling pump motor #02 disconnector switch | IFI | - | -
Hydraulic energy sources remote I/O: technical room | - | r43.61-5521-GEN-ESR40-RIO01 | r43.61-5521-GEN-ESR40-RIO01-WC06 | CWC01 | 2x1 | 10 | YSLY 300/500V | - | r43.61-5521-GEN-ESR40-DSS06 | - | Oil heater #01 disconnector switch | IFI | - | -
Hydraulic pump motor #01 disconnector switch | - | r43.61-5521-GEN-ESR40-DSS01 | r43.61-5521-GEN-ESR40-DSS01-WP01 | CWP02 | 4G10+SH | 4 | RC4V-K 0,6/1kV | - | r41,63-5521-GEN-ESR40-HYG01-M01 | Hydraulic pump motor #01 | - | IFI | - | -
Hydraulic pump motor #02 disconnector switch | - | r43.61-5521-GEN-ESR40-DSS02 | r43.61-5521-GEN-ESR40-DSS02-WP01 | CWP02 | 4G10+SH | 4 | RC4V-K 0,6/1kV | - | r41,63-5521-GEN-ESR40-HYG01-M02 | Hydraulic pump motor #02 | - | IFI | - | -
Hydraulic pump motor #03 disconnector switch | - | r43.61-5521-GEN-ESR40-DSS03 | r43.61-5521-GEN-ESR40-DSS03-WP01 | CWP02 | 4G10+SH | 4 | RC4V-K 0,6/1kV | - | r41,63-5521-GEN-ESR40-HYG01-M03 | Hydraulic pump motor #03 | - | IFI | - | -
Hydraulic cooling pump motor #01 disconnector switch | - | r43.61-5521-GEN-ESR40-DSS04 | r43.61-5521-GEN-ESR40-DSS04-WP01 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | r41,63-5521-GEN-ESR40-COO01-M01 | Hydraulic group cooling pump motor #01 | - | IFI | - | -
Hydraulic cooling pump motor #02 disconnector switch | - | r43.61-5521-GEN-ESR40-DSS05 | r43.61-5521-GEN-ESR40-DSS05-WP01 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | r41,63-5521-GEN-ESR40-COO01-M02 | Hydraulic group cooling pump motor #02 | - | IFI | - | -
Oil heater #01 disconnector switch | - | r43.61-5521-GEN-ESR40-DSS06 | r43.61-5521-GEN-ESR40-DSS06-WP01 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | r41,63-5521-GEN-ESR40-HTE01-H01 | Oil heater #01 | - | IFI | - | -
Hydraulic energy sources remote I/O: technical room | - | r43.61-5521-GEN-ESR40-RIO01 | r43.61-5521-GEN-ESR40-RIO01-WE01 | CWE02 | SF/UTP | 63 | 6XV1840-2AH10 | - | r43.61-5521-GEN-ESR40-PCP01 | - | Hydraulic main power control panel | AIB | - | -
Hydraulic energy sources remote I/O: technical room | - | r43.61-5521-GEN-ESR40-RIO01 | r43.61-5521-GEN-ESR40-RIO01-WC10 | CWC01 | 24G1 | 10 | YSLY 300/500V | - | r43.61-5521-GEN-ESR40-IJB01 | - | Hydraulic main instrumentation junction box | IFI | - | -
Hydraulic energy sources remote I/O: technical room | - | r43.61-5521-GEN-ESR40-RIO01 | r43.61-5521-GEN-ESR40-RIO01-WE03 | CWE02 | SF/UTP | 10 | 6XV1840-2AH10 | - | r43.61-5521-GEN-ESR40-IJB01 | - | Hydraulic main instrumentation junction box | IFI | - | -
Hydraulic energy sources remote I/O: technical room | - | r43.61-5521-GEN-ESR40-RIO01 | r43.61-5521-GEN-ESR40-RIO01-WC12 | CWC01 | 24G1 | 10 | YSLY 300/500V | - | r43.61-5521-GEN-ESR40-IJB02 | - | 3321 TMT hydraulic valves instrumentation junction box | IFI | - | -
Hydraulic energy sources remote I/O: technical room | - | r43.61-5521-GEN-ESR40-RIO01 | r43.61-5521-GEN-ESR40-RIO01-WE05 | CWE02 | SF/UTP | 10 | 6XV1840-2AH10 | - | r43.61-5521-GEN-ESR40-IJB02 | - | 3321 TMT hydraulic valves instrumentation junction box | IFI | - | -
Hydraulic energy sources remote I/O: technical room | - | r43.61-5521-GEN-ESR40-RIO01 | r43.61-5521-GEN-ESR40-RIO01-WC11 | CWC01 | 24G1 | 10 | YSLY 300/500V | - | r43.61-5521-GEN-ESR40-IJB03 | - | 3321 THD hydraulic valves instrumentation junction box | IFI | - | -
Hydraulic energy sources remote I/O: technical room | - | r43.61-5521-GEN-ESR40-RIO01 | r43.61-5521-GEN-ESR40-RIO01-WE04 | CWE02 | SF/UTP | 10 | 6XV1840-2AH10 | - | r43.61-5521-GEN-ESR40-IJB03 | - | 3321 THD hydraulic valves instrumentation junction box | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC01 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0401A | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC02 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0402A | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC03 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0403A | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC04 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0404A | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC05 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0405A | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC06 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0406A | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC07 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0407A | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC08 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0408A | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC09 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0409A | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC11 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0401B | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC12 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0402B | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC13 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0403B | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC14 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0404B | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC15 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0405B | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC16 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0406B | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC17 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0407B | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC18 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0408B | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC19 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0409B | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC20 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-SV0416 | Solenoid valve | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC21 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-LTI0401 | Level and Temperature Sensor | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC22 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB01-ZS0401 | Safety level switch | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC30 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-PT401 | Pressure transmiter | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC31 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-PT402 | Pressure transmiter | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC32 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-PT403 | Pressure transmiter | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC33 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-PDT0401 | Diferential pressure transmiter | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC34 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-PDT0402 | Diferential pressure transmiter | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC35 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-PDT0403 | Diferential pressure transmiter | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC36 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-PDT0404 | Diferential pressure transmiter | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC37 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-PDT0407 | Diferential pressure transmiter | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC38 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-PDT0408 | Diferential pressure transmiter | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC39 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-PDT0409 | Diferential pressure transmiter | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC40 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-PDT0410 | Diferential pressure transmiter | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC41 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-PDT0413 | Diferential pressure transmiter | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC42 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-PDT0414 | Diferential pressure transmiter | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC43 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-TS0401 | Motor temperature switch PTC M01 | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC44 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-TS0402 | Motor temperature switch PTC M02 | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC45 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-TS0403 | Motor temperature switch PTC M03 | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC46 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-TE0401 | Motor temperature M01 | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC47 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-TE0402 | Motor temperature M02 | - | IFI | - | -
Hydraulic main instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB01 | r43.61-5521-GEN-ESR40-IJB01-WC48 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB01-TE0403 | Motor temperature M03 | - | IFI | - | -
3321 THD hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB03 | r43.61-5521-GEN-ESR40-IJB03-WC01 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB03-SV0401A | Solenoid valve | - | IFI | - | -
3321 THD hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB03 | r43.61-5521-GEN-ESR40-IJB03-WC02 | CWC02 | 7G1+SH | 1 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB03-SV0404 | Solenoid valve | - | IFI | - | -
3321 THD hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB03 | r43.61-5521-GEN-ESR40-IJB03-WC03 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB03-SV0401B | Solenoid valve | - | IFI | - | -
3321 THD hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB03 | r43.61-5521-GEN-ESR40-IJB03-WC04 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB03-SV0402 | Solenoid valve | - | IFI | - | -
3321 THD hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB03 | r43.61-5521-GEN-ESR40-IJB03-WC05 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB03-SV0403 | Solenoid valve | - | IFI | - | -
3321 THD hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB03 | r43.61-5521-GEN-ESR40-IJB03-WC06 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB03-PT0401 | Pressure transmiter | - | IFI | - | -
3321 THD hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB03 | r43.61-5521-GEN-ESR40-IJB03-WC07 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB03-PT0402 | Pressure transmiter | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC09 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB02-SV0401A | Solenoid valve | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC10 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB02-SV0402A | Solenoid valve | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC11 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB02-SV0401B | Solenoid valve | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC12 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB02-SV0402B | Solenoid valve | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC13 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB02-SV0403A | Solenoid valve | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC14 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB02-SV0403B | Solenoid valve | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC15 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB02-SV0404 | Solenoid valve | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC16 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5521-GEN-ESR40-IJB02-SV0405 | Solenoid valve | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC17 | CWC02 | 7G1+SH | 1 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB02-SV0406 | Servo valve | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC20 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB02-PT0401 | Pressure transmiter | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC21 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB02-PT0402 | Pressure transmiter | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC22 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB02-PT0403 | Pressure transmiter | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC23 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB02-PT0404 | Pressure transmiter | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC24 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB02-PT0405 | Pressure transmiter | - | IFI | - | -
3321 TMT hydraulic valves instrumentation junction box | - | r43.61-5521-GEN-ESR40-IJB02 | r43.61-5521-GEN-ESR40-IJB02-WC25 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5521-GEN-ESR40-IJB02-PT0406 | Pressure transmiter | - | IFI | - | -