## Cover
Client: |  | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
Cover
CUSTOMER: |  | ALINVEST | PREPARED: | JOBI
PROJECT CODE: |  | E2558 | REVIEWED: | ANSA
PROJECT NAME: |  | ALFAGEN | DATE: | 2025/12/04
CONTRACTOR DOC. CODE: |  | 2558-5523-GEN-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: |  | 2558-5523-GEN-E-LST-CBLS | PAGE: | 01 of 04
REVISION CONTROL
REV | DATE | DESCRIPTON |  | PAGE
A | 2025/12/01 | Issue for information |  | 1-4
B
C
D
E
F
G
H
I
J
K
L
M
N
O
P
Q
R
S
T
U
V
W
X
Y
Z
AA
AB
AC
AD
AE
The drawing(s), document(s) and the information contained herein are the property of INDUSTRIAL FURNACES INSERTEC. And they shall not be disclosed, reproduced or used in any manner without the prior written consent of INDUSTRIAL FURNACES INSERTEC. Offenders will be held liable for the payment of damages.

## Table of Contents
Client: |  | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
Table of contents
CUSTOMER: |  | ALINVEST | PREPARED: | JOBI
PROJECT CODE: |  | E2558 | REVIEWED: | ANSA
PROJECT NAME: |  | ALFAGEN | DATE: | 2025/12/04
CONTRACTOR DOC. CODE: |  | 2558-5523-GEN-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: |  | 2558-5523-GEN-E-LST-CBLS | PAGE: | 02 of 04
Table of contents
SEC | DESCRIPTON |  |  | PAGE
0 | Cover |  |  | 1
1 | Table of contents |  |  | 2
2 | Definitions |  |  | 3
3 | Equipment cable list |  |  | 4
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
The drawing(s), document(s) and the information contained herein are the property of INDUSTRIAL FURNACES INSERTEC. And they shall not be disclosed, reproduced or used in any manner without the prior written consent of INDUSTRIAL FURNACES INSERTEC. Offenders will be held liable for the payment of damages.

## Definitions
Client: | EQUIPMENT CABLE LIST | Contractor:
ALINVEST
DEFINITIONS
CUSTOMER: | ALINVEST | PREPARED: | JOBI
PROJECT CODE: | E2558 | REVIEWED: | ANSA
PROJECT NAME: | ALFAGEN | DATE: | 2025/12/04
CONTRACTOR DOC. CODE: | 2558-5523-GEN-E-LST-CBLS | REVISION: | A
CUSTOMER DOC. CODE: | 2558-5523-GEN-E-LST-CBLS | PAGE: | 03 of 04
MAIN DEFINITIONS
== -
= -
++ -
+ -
Description -
IME (Complete) -
Tag - For more detail, please refer to B001-B002-GEN-E-PRC-NPOS-R09 Numbering procedure for electrical objects and signals document.
Category - For more detail, please refer to B001-B002-GNL-E-SPC-INCC-R02 Technical specification for cables and cable trays document.
Type - Cable type according to conductor number, section, shield, etc
Length - Estimated lenght of the given cable.
Page - Page number realted to the electrical schematics. Refer to: B001-B002-B003-E-DWG-ESCH-R00 Equipment electrical schematics
Function -
Remarks - Notes to be considered.
Revision change comments - Revision change reason comments.

## Equipment cable list
Client: | CUSTOMER: | ALINVEST |  | EQUIPMENT CABLE LIST | [7 empty] | PREPARED: | JOBI | Contractor:
ALINVEST | PROJECT CODE: | E2558 | [9 empty] | REVIEWED: | ANSA
| PROJECT NAME: | ALFAGEN | [9 empty] | DATE: | 2025/12/04
| CONTRACTOR DOC. CODE: | 2558-5523-GEN-E-LST-CBLS | [9 empty] | REVISION: | A
| CUSTOMER DOC. CODE: | 2558-5523-GEN-E-LST-CBLS | [9 empty] | PAGE: | 04 of 04
SOURCE |  |  | CABLE | [5 empty] | DESTINATION |  |  | OTHERS
Location Description | Instrument Description | Device Tag | Tag | Category | Type | Length [m] | Cable Reference | Route | Device Tag | Instrument Description | Location Description | Scope of Supply | Remarks | Revision Change Comment
T145.61 | - | r45.61 | WL45.61.R1 | CWP01 | 1x95 | TBD BY CLIENT | - | - | r45.61-5523-GEN-ESR40-PCP01 | - | - | AIB
T145.61 | - | r45.61 | WL45.61.S1 | CWP01 | 1x95 | TBD BY CLIENT | - | - | r45.61-5523-GEN-ESR40-PCP01 | - | - | AIB
T145.61 | - | r45.61 | WL45.61.T1 | CWP01 | 1x95 | TBD BY CLIENT | - | - | r45.61-5523-GEN-ESR40-PCP01 | - | - | AIB
T145.61 | - | r45.61 | WL45.61.P1 | CWP01 | 1x95 PE | TBD BY CLIENT | - | - | r45.61-5523-GEN-ESR40-PCP01 | - | - | AIB
T145.61 | - | r45.61 | WL45.61.L1 | CWP01 | 3G2,5 | TBD BY CLIENT | - | - | r45.61-5523-GEN-ESR40-PCP01 | - | - | AIB
T145.61 | - | r45.61 | WL45.61.R2 | CWP01 | 1x95 | TBD BY CLIENT | - | - | FUTURE LINE | - | - | AIB
T145.61 | - | r45.61 | WL45.61.S2 | CWP01 | 1x95 | TBD BY CLIENT | - | - | FUTURE LINE | - | - | AIB
T145.61 | - | r45.61 | WL45.61.T2 | CWP01 | 1x95 | TBD BY CLIENT | - | - | FUTURE LINE | - | - | AIB
T145.61 | - | r45.61 | WL45.61.P2 | CWP01 | 1x95 PE | TBD BY CLIENT | - | - | FUTURE LINE | - | - | AIB
T145.61 | - | r45.61 | WL45.61.L2 | CWP01 | 3G2,5 | TBD BY CLIENT | - | - | FUTURE LINE | - | - | AIB
Hydraulic main power control panel | - | r45.61-5523-GEN-ESR40-PCP01 | r45.61-5523-GEN-ESR40-PCP01-WP01 | CWP02 | 4G10+SH | 106 | RC4V-K 0,6/1kV | - | r45.61-5523-GEN-ESR40-DSS01 | - | Hydraulic pump motor #01 disconnector switch | AIB
Hydraulic main power control panel | - | r45.61-5523-GEN-ESR40-PCP01 | r45.61-5523-GEN-ESR40-PCP01-WP02 | CWP02 | 4G10+SH | 106 | RC4V-K 0,6/1kV | - | r45.61-5523-GEN-ESR40-DSS02 | - | Hydraulic pump motor #02 disconnector switch | AIB
Hydraulic main power control panel | - | r45.61-5523-GEN-ESR40-PCP01 | r45.61-5523-GEN-ESR40-PCP01-WP03 | CWP02 | 4G10+SH | 106 | RC4V-K 0,6/1kV | - | r45.61-5523-GEN-ESR40-DSS03 | - | Hydraulic pump motor #03 disconnector switch | AIB
Hydraulic main power control panel | - | r45.61-5523-GEN-ESR40-PCP01 | r45.61-5523-GEN-ESR40-PCP01-WP04 | CWP01 | 4G2,5 | 106 | RV-K 0,6/1kV | - | r45.61-5523-GEN-ESR40-DSS04 | - | Hydraulic cooling pump motor #01 disconnector switch | AIB
Hydraulic main power control panel | - | r45.61-5523-GEN-ESR40-PCP01 | r45.61-5523-GEN-ESR40-PCP01-WP05 | CWP01 | 4G2,5 | 106 | RV-K 0,6/1kV | - | r45.61-5523-GEN-ESR40-DSS05 | - | Hydraulic cooling pump motor #02 disconnector switch | AIB
Hydraulic main power control panel | - | r45.61-5523-GEN-ESR40-PCP01 | r45.61-5523-GEN-ESR40-PCP01-WP06 | CWP01 | 4G2,5 | 106 | RV-K 0,6/1kV | - | r45.61-5523-GEN-ESR40-DSS06 | - | Oil heater #01 disconnector switch | AIB
Hydraulic main power control panel | - | r45.61-5523-GEN-ESR40-PCP01 | r45.61-5523-GEN-ESR40-PCP01-WP07 | CWP01 | 3G2,5 | 108 | RV-K 0,6/1kV | - | r45.61-5523-GEN-ESR40-RIO01 | Hydraulic energy sources remote I/O: technical room | - | AIB
Hydraulic main power control panel | - | r45.61-5523-GEN-ESR40-PCP01 | r45.61-5523-GEN-ESR40-PCP01-WP08 | CWP01 | 3G2,5 | 108 | RV-K 0,6/1kV | - | r45.61-5523-GEN-ESR40-RIO01 | Hydraulic energy sources remote I/O: technical room | - | AIB
Hydraulic main power control panel | - | r45.61-5523-GEN-ESR40-PCP01 | r45.61-5523-GEN-ESR40-PCP01-WE02 | CWE02 | SF/UTP | 108 | 6XV1840-2AH10 | - | r45.61-5523-GEN-ESR40-RIO01 | Hydraulic energy sources remote I/O: technical room | - | AIB
Hydraulic energy sources remote I/O: technical room | - | r45.61-5523-GEN-ESR40-RIO01 | r45.61-5523-GEN-ESR40-RIO01-WC01 | CWC01 | 2x1 | 10 | YSLY 300/500V | - | r45.61-5523-GEN-ESR40-DSS01 | - | Hydraulic pump motor #01 disconnector switch | IFI
Hydraulic energy sources remote I/O: technical room | - | r45.61-5523-GEN-ESR40-RIO01 | r45.61-5523-GEN-ESR40-RIO01-WC02 | CWC01 | 2x1 | 10 | YSLY 300/500V | - | r45.61-5523-GEN-ESR40-DSS02 | - | Hydraulic pump motor #02 disconnector switch | IFI
Hydraulic energy sources remote I/O: technical room | - | r45.61-5523-GEN-ESR40-RIO01 | r45.61-5523-GEN-ESR40-RIO01-WC03 | CWC01 | 2x1 | 10 | YSLY 300/500V | - | r45.61-5523-GEN-ESR40-DSS03 | - | Hydraulic pump motor #03 disconnector switch | IFI
Hydraulic energy sources remote I/O: technical room | - | r45.61-5523-GEN-ESR40-RIO01 | r45.61-5523-GEN-ESR40-RIO01-WC04 | CWC01 | 2x1 | 10 | YSLY 300/500V | - | r45.61-5523-GEN-ESR40-DSS04 | - | Hydraulic cooling pump motor #01 disconnector switch | IFI
Hydraulic energy sources remote I/O: technical room | - | r45.61-5523-GEN-ESR40-RIO01 | r45.61-5523-GEN-ESR40-RIO01-WC05 | CWC01 | 2x1 | 10 | YSLY 300/500V | - | r45.61-5523-GEN-ESR40-DSS05 | - | Hydraulic cooling pump motor #02 disconnector switch | IFI
Hydraulic energy sources remote I/O: technical room | - | r45.61-5523-GEN-ESR40-RIO01 | r45.61-5523-GEN-ESR40-RIO01-WC06 | CWC01 | 2x1 | 10 | YSLY 300/500V | - | r45.61-5523-GEN-ESR40-DSS06 | - | Oil heater #01 disconnector switch | IFI
Hydraulic pump motor #01 disconnector switch | - | r45.61-5523-GEN-ESR40-DSS01 | r45.61-5523-GEN-ESR40-DSS01-WP01 | CWP02 | 4G10+SH | 4 | RC4V-K 0,6/1kV | - | r41,63-5523-GEN-ESR40-HYG01-M01 | Hydraulic pump motor #01 | - | IFI
Hydraulic pump motor #02 disconnector switch | - | r45.61-5523-GEN-ESR40-DSS02 | r45.61-5523-GEN-ESR40-DSS02-WP01 | CWP02 | 4G10+SH | 4 | RC4V-K 0,6/1kV | - | r41,63-5523-GEN-ESR40-HYG01-M02 | Hydraulic pump motor #02 | - | IFI
Hydraulic pump motor #03 disconnector switch | - | r45.61-5523-GEN-ESR40-DSS03 | r45.61-5523-GEN-ESR40-DSS03-WP01 | CWP02 | 4G10+SH | 4 | RC4V-K 0,6/1kV | - | r41,63-5523-GEN-ESR40-HYG01-M03 | Hydraulic pump motor #03 | - | IFI
Hydraulic cooling pump motor #01 disconnector switch | - | r45.61-5523-GEN-ESR40-DSS04 | r45.61-5523-GEN-ESR40-DSS04-WP01 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | r41,63-5523-GEN-ESR40-COO01-M01 | Hydraulic group cooling pump motor #01 | - | IFI
Hydraulic cooling pump motor #02 disconnector switch | - | r45.61-5523-GEN-ESR40-DSS05 | r45.61-5523-GEN-ESR40-DSS05-WP01 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | r41,63-5523-GEN-ESR40-COO01-M02 | Hydraulic group cooling pump motor #02 | - | IFI
Oil heater #01 disconnector switch | - | r45.61-5523-GEN-ESR40-DSS06 | r45.61-5523-GEN-ESR40-DSS06-WP01 | CWP01 | 4G2,5 | 4 | RV-K 0,6/1kV | - | r41,63-5523-GEN-ESR40-HTE01-H01 | Oil heater #01 | - | IFI
Hydraulic energy sources remote I/O: technical room | - | r45.61-5523-GEN-ESR40-RIO01 | r45.61-5523-GEN-ESR40-RIO01-WE01 | CWE02 | SF/UTP | 108 | 6XV1840-2AH10 | - | r45.61-5523-GEN-ESR40-PCP01 | - | Hydraulic main power control panel | AIB
Hydraulic energy sources remote I/O: technical room | - | r45.61-5523-GEN-ESR40-RIO01 | r45.61-5523-GEN-ESR40-RIO01-WC10 | CWC01 | 24G1 | 10 | YSLY 300/500V | - | r45.61-5523-GEN-ESR40-IJB01 | - | Hydraulic main instrumentation junction box | IFI
Hydraulic energy sources remote I/O: technical room | - | r45.61-5523-GEN-ESR40-RIO01 | r45.61-5523-GEN-ESR40-RIO01-WE03 | CWE02 | SF/UTP | 10 | 6XV1840-2AH10 | - | r45.61-5523-GEN-ESR40-IJB01 | - | Hydraulic main instrumentation junction box | IFI
Hydraulic energy sources remote I/O: technical room | - | r45.61-5523-GEN-ESR40-RIO01 | r45.61-5523-GEN-ESR40-RIO01-WC12 | CWC01 | 24G1 | 10 | YSLY 300/500V | - | r45.61-5523-GEN-ESR40-IJB02 | - | 3321 TMT hydraulic valves instrumentation junction box | IFI
Hydraulic energy sources remote I/O: technical room | - | r45.61-5523-GEN-ESR40-RIO01 | r45.61-5523-GEN-ESR40-RIO01-WE05 | CWE02 | SF/UTP | 10 | 6XV1840-2AH10 | - | r45.61-5523-GEN-ESR40-IJB02 | - | 3321 TMT hydraulic valves instrumentation junction box | IFI
Hydraulic energy sources remote I/O: technical room | - | r45.61-5523-GEN-ESR40-RIO01 | r45.61-5523-GEN-ESR40-RIO01-WC11 | CWC01 | 24G1 | 10 | YSLY 300/500V | - | r45.61-5523-GEN-ESR40-IJB03 | - | 3321 THD hydraulic valves instrumentation junction box | IFI
Hydraulic energy sources remote I/O: technical room | - | r45.61-5523-GEN-ESR40-RIO01 | r45.61-5523-GEN-ESR40-RIO01-WE04 | CWE02 | SF/UTP | 10 | 6XV1840-2AH10 | - | r45.61-5523-GEN-ESR40-IJB03 | - | 3321 THD hydraulic valves instrumentation junction box | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC01 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0401A | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC02 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0402A | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC03 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0403A | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC04 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0404A | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC05 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0405A | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC06 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0406A | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC07 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0407A | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC08 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0408A | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC09 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0409A | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC11 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0401B | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC12 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0402B | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC13 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0403B | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC14 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0404B | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC15 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0405B | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC16 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0406B | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC17 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0407B | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC18 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0408B | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC19 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0409B | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC20 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-SV0416 | Solenoid valve | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC21 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-LTI0401 | Level and Temperature Sensor | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC22 | CWC01 | 3G1 | 4 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB01-ZS0401 | Safety level switch | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC30 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-PT401 | Pressure transmiter | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC31 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-PT402 | Pressure transmiter | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC32 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-PT403 | Pressure transmiter | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC33 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-PDT0401 | Diferential pressure transmiter | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC34 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-PDT0402 | Diferential pressure transmiter | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC35 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-PDT0403 | Diferential pressure transmiter | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC36 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-PDT0404 | Diferential pressure transmiter | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC37 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-PDT0407 | Diferential pressure transmiter | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC38 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-PDT0408 | Diferential pressure transmiter | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC39 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-PDT0409 | Diferential pressure transmiter | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC40 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-PDT0410 | Diferential pressure transmiter | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC41 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-PDT0413 | Diferential pressure transmiter | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC42 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-PDT0414 | Diferential pressure transmiter | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC43 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-TS0401 | Motor temperature switch PTC M01 | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC44 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-TS0402 | Motor temperature switch PTC M02 | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC45 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-TS0403 | Motor temperature switch PTC M03 | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC46 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-TE0401 | Motor temperature M01 | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC47 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-TE0402 | Motor temperature M02 | - | IFI
Hydraulic main instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB01 | r45.61-5523-GEN-ESR40-IJB01-WC48 | CWC02 | 4X1+SH | 4 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB01-TE0403 | Motor temperature M03 | - | IFI
3323 THD hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB03 | r45.61-5523-GEN-ESR40-IJB03-WC01 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB03-SV0401A | Solenoid valve | - | IFI
3323 THD hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB03 | r45.61-5523-GEN-ESR40-IJB03-WC02 | CWC02 | 7G1+SH | 1 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB03-SV0404 | Solenoid valve | - | IFI
3323 THD hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB03 | r45.61-5523-GEN-ESR40-IJB03-WC03 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB03-SV0401B | Solenoid valve | - | IFI
3323 THD hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB03 | r45.61-5523-GEN-ESR40-IJB03-WC04 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB03-SV0402 | Solenoid valve | - | IFI
3323 THD hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB03 | r45.61-5523-GEN-ESR40-IJB03-WC05 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB03-SV0403 | Solenoid valve | - | IFI
3323 THD hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB03 | r45.61-5523-GEN-ESR40-IJB03-WC06 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB03-PT0401 | Pressure transmiter | - | IFI
3323 THD hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB03 | r45.61-5523-GEN-ESR40-IJB03-WC07 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB03-PT0402 | Pressure transmiter | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC09 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB02-SV0401A | Solenoid valve | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC10 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB02-SV0402A | Solenoid valve | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC11 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB02-SV0401B | Solenoid valve | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC12 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB02-SV0402B | Solenoid valve | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC13 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB02-SV0403A | Solenoid valve | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC14 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB02-SV0403B | Solenoid valve | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC15 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB02-SV0404 | Solenoid valve | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC16 | CWC01 | 3G1 | 1 | YSLY 300/500V | - | 5523-GEN-ESR40-IJB02-SV0405 | Solenoid valve | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC17 | CWC02 | 7G1+SH | 1 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB02-SV0406 | Servo valve | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC20 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB02-PT0401 | Pressure transmiter | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC21 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB02-PT0402 | Pressure transmiter | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC22 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB02-PT0403 | Pressure transmiter | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC23 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB02-PT0404 | Pressure transmiter | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC24 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB02-PT0405 | Pressure transmiter | - | IFI
3323 TMT hydraulic valves instrumentation junction box | - | r45.61-5523-GEN-ESR40-IJB02 | r45.61-5523-GEN-ESR40-IJB02-WC25 | CWC02 | 4X1+SH | 1 | RC4V-K 300/500V | - | 5523-GEN-ESR40-IJB02-PT0406 | Pressure transmiter | - | IFI