## Changelog
Changelog
|  | change |  | transmitted
Revision | Change | Who | Date | Who | Date
Rev 0 | first creation | VIT | 2024-10-01 | VIT | 2024-10-18
Rev1 | updated volumes / pressure / supply data updated filterbox + tundish preheat TOPs updated exhaust systems + ARP TOPs | VIT VIT VIT | 25.11.2024 26.11.2024 28.11.2024 | VIT | 2024-11-29
Rev2 | correcting ARP data Extending HPI Main supply cabinet and its distribution correcting current supply CD according data of first offer added evaporation of cooling water changed BLT water TOP´s to 3 bar (W5, W8, W10), added BLT cooling water backflow (W6, W9, W11) eliminated TOP C4 casting machine changed TOP C1 to whole casting line TOP X3 - will be blown into the building added TOP X4 - exhaust air compressor chip suction system changed values into ranges hiding old electrical top's added coordinates infos to all TOP's directions for connection changed to AIB specs. data changes at A10 + A11 changed direction at G1 & C8 & C9 & C10 refined degasser gas supply Argon + Chlorine + gas supply DC added AIB TOP ID changed standards of pipes adding cable type of electrical supply EH, EB according AIB_HPI_M037 added C11 | ZIC ZIC ZIC VIT ZIM VIT VIT VIT VIT VIT ZIC VIT VIT VIT VIT VIT VIT VIT ZIC VIT | 01.12.2024 15.12.2024 15.12.2024 15.01.2025 24.02.2025 25.02.2025 25.02.2025 13.03.2025 13.03.2025 14.03.2025 21.03.2025 24.03.2025 24.03.2025 24.03.2025 24.03.2025 2403.2025 26.03.2025 26.03.2025 28.03.2025 31.03.2025 | VIT | 2025-04-03
Rev3 | added detail infos for degasser exhaust W1 cooling water diagramm revisioned | VIT VIT | 23.04.2025 29.04.2025 | VIT | 2025-04-30
Rev4 | electrical top of 230 VAC for light and socket added - AIB request correcting power supply of 400 VAC from PE + N to PEN C11 changed needed pressure W1 changed revision of PID E91 - E98 added mouldshop electric C91 - C93 added mouldshop compressed air W90 & W91 - added position information mouldshop water (suggestion) A1 - eliminated chlorine gas TOP several changes due to AIB media pressures | ZIC ZIC VIT VIT VIT VIT VIT VIT VIT | 02.06.2025 02.06.2025 03.06.2025 01.07.2025 28.07.2025 28.07.2025 28.07.2025 28.07.2025 28.07.2025 | VIT | 2025-07-30
Rev5 | A2 + A3 changed datas (chlorine elimination) A4 eliminated (no more chlorine) A10 + A11 changed flow / pressure datas, added pipe definition A20+A21 added completely C6+C8+C9+C10 changed needed pressure | VIT VIT VIT VIT VIT | 06.08.2025 06.08.2025 06.08.2025 06.08.2025 19.08.2025 | VIT | 2025-09-02
Rev6 | A2 + A3 added max. supply pressure X1 added position informations + connection G2 changed connection size | VIT VIT VIT | 11.09.2025 15.09.2025 15.09.2025 | VIT | 2025-09-29
Rev7 | Adding electrical connection points for AIB supplied cables | ZIC | 2025-10-10
Rev8
Rev9
Abbreviations used for direction
|  | North | N
|  | South | S
|  | East | E
|  | West | W
|  | Top | T
|  | Bottom | B

## TOP
TAKE OVER POINTS (TOP's) - 390 - Al Invest | [11 empty] | REV 7 --- xx.xx.2025
TOP electricity
No | AIB No. | (Sub) Supplier(s) | Description | Requirement | [10 empty] | Remark
|  |  |  | I [A] | U [V] | Circuit breaker | Main wire (per phase) | Ground wire | Definition | Connector | Connection by | X [mm] (from Ref. point AIB) | Y [mm] (from Ref. point AIB) | Z [mm] (from shop floor +-0)
EH | 903 | HPI | Casting Line | 1000 | 400 | 1300 | 4 x 3x240 | 4 x 1x120 | 400Y/230VAC/50Hz/3Φ/3W+GND | 3/PEN | input B --> T | 44462 | 7958 | 500 | Distributing 4 x 160 A, 3 x 250 A, 2 x 400 A 4 cables (1-AYKY 3x240 + 120) aluminium
|  | +N02.CA001 | Main supply 160 A | [11 empty] | Spare
|  | +N02.CB001 | Main supply 160 A | 35 | [10 empty] | Supplying Dynamic Concept
|  | +N02.DB001 | Main supply 160 A | 100 | [10 empty] | Supplying Pyrotek
|  | +N02.EA001 | Main supply 160 A | 125 | [10 empty] | Supplying +HMC.AS (UPS)
|  | +N02.FB001 | Main supply 250 A | [11 empty] | Spare
|  | +N02.HA001 | Main supply 250 A | 125 | [10 empty] | Supplying ARP 1
|  | +N02.JB001 | Main supply 250 A | 200 | [10 empty] | Supplying +HCS.CS Casting system
|  | +N02.LB001 | Main supply 400 A | 160 | [10 empty] | Supplying ARP 2
|  | +N02.PB001 | Main supply 400 A | 250 | [10 empty] | Supplying =04+HMC.MS Casting Line
EB | 904 | Bültmann & KD | Ultrasonic inspection + Peeling | 800 | 400 | 1000 | 3 x 3x240 | 3 x 1x120 | 400Y/230VAC/50Hz/3Φ/3W+GND | 3/PEN | input B --> T | 58366 | 7958 | 500 | 3 cables (1-AYKY 3x240 + 120) aluminium
|  | ARP / RUF | Chip treatment and briquetting | 121 | 400 | tbd | tbd | tbd | 400Y/230VAC/50Hz/3Φ/4W+GND | 3/N/PE | input B --> T |  |  |  | distribution of TOP by HPI
|  | Dynamic Concept | Filterbox Dynaprime | 30 | 400 | tbd | tbd | tbd | 400Y/230VAC/50Hz/3Φ/4W+GND | 3/PE | input B --> T |  |  |  | distribution of TOP by HPI
|  | Pyrotek | Degasser SNIF | 72 | 400 | tbd | tbd | tbd | 400Y/230VAC/50Hz/3Φ/4W+GND | [5 empty] | distribution of TOP by HPI
|  | Promeos | Tundish preheating system | 9 | 400 | tbd | tbd | tbd | 400Y/230VAC/50Hz/3Φ/4W+GND | 3/PE | input B --> T |  |  |  | distribution of TOP by HPI
=04+HMC.MS |  | HPI | Casting line main supply
+HMC.CM |  | HPI | Casting line casting machine
|  | HPI | Lights and plug sockets | 63 | 230 | tbd | tbd | tbd | 120VAC/60Hz/1Φ/2W + GND | 1/N/PE |  |  |  |  | distribution of TOP by HPI
|  | Bültmann | Lights and plug sockets | 63 | 230 | tbd | tbd | tbd | 120VAC/60Hz/1Φ/2W + GND | 1/N/PE |  |  |  |  | distribution of TOP by HPI
|  | ARP | Lights and plug sockets | tbd | 230 | tbd | tbd | tbd | 120VAC/60Hz/1Φ/2W + GND | 1/N/PE | input B --> T |  |  |  | distribution of TOP by HPI
|  | ARP | Chips central | 125 | 400 | [5 empty] | input B --> T |  |  |  | distribution of TOP by HPI (40kW main cabinet / 22kW briquetting press / 37kW vacuum blower / 0,75kW screw conveyor)
|  | ARP | suction point: flying saw | 16 | 400 | [5 empty] | input B --> T |  |  |  | distribution of TOP by HPI (1kW cabinet / 0,25kW suction unit)
|  | ARP | suction point: peeling machine | 80 | 400 | [5 empty] | input B --> T |  |  |  | distribution of TOP by HPI (25kW cabinet / 0,37kW screw conveyor / 0,25kW dosing screw / 5,5kW centrifuge / 0,25kW suction unit / 2x7,5kW shredder)
|  | ARP | suction point: uncontrolled ends | 16 | 400 | [5 empty] | input B --> T |  |  |  | distribution of TOP by HPI (3kW cabinet / 0,25kW suction unit / 2,2kW shredder)
|  | ARP / RUF | Briquetting press | 32 | 400 | [5 empty] | input B --> T |  |  |  | distribution of TOP by HPI
S)= |  | Al Invest | House electric mouldshop | tbd | 230 | tbd
EH2 |  | HPI | Light and socket of casting line | 63 | 230 |  |  |  | 230VAC/50Hz/1Φ/2W+GND | L+N+PE | input B --> T | 70262 | 7958 | 500
EB2 |  | Bültmann & KD | Light and socket of ultasonic and peeling area | 63 | 230 |  |  |  | 230VAC/50Hz/1Φ/2W+GND | L+N+PE | input B --> T | 58366 | 7958 | 500
E91 |  | Al Invest | Mouldshop | 63 | 400 / 230 | [5 empty] | input T --> B | 53766 | 27939 | 1200 | HPI suggestion for TOP's E91 - E98: installing on each point typical socket distributor 1x 400 VAC/32A 1x 400 VAC/16A 3-5x 230 VAC/13A
E92 |  | Al Invest | Mouldshop | 63 | 400 / 230 | [5 empty] | input T --> B | 53766 | 29039 | 1200
E93 |  | Al Invest | Mouldshop | 63 | 400 / 230 | [5 empty] | input T --> B | 41850 | 28489 | 1200
E94 |  | Al Invest | Mouldshop | 63 | 400 / 230 | [5 empty] | input T --> B | 46680 | 33079 | 1200
E95 |  | Al Invest | Mouldshop | 63 | 400 / 230 | [5 empty] | input T --> B | 52095 | 33079 | 1200
E96 |  | Al Invest | Mouldshop | 63 | 400 / 230 | [5 empty] | input T --> B | 46680 | 23899 | 1200
E97 |  | Al Invest | Mouldshop | 63 | 400 / 230 | [5 empty] | input T --> B | 52095 | 23899 | 1200
E98 |  | Al Invest | Mouldshop | 63 | 400 / 230 | [5 empty] | input T --> B | 57610 | 28249 | 1200
EP10 |  | Al Invest | Power supply for Pyrotek inert gas panel |  | 230 |  | 3G2,5 |  |  |  | input B --> T | 85962 | 7958 | 1600
EP20 |  | Al Invest | Communication cable to remote station inert gas panel | NA | NA |  | Fibre optic multimode |  |  |  | input B --> T | 85962 | 7958 | 1800
EP11 |  | Al Invest | Power supply receiving on Pyrotek inert gas panel |  | 230 |  | 3G2,5 |  |  |  | input B --> T | NA | NA | 2000 | Position of inert gas panel is not clear, therefore position is not available
EP21 |  | Al Invest | Communication cable to remote station inert gas panel | NA | NA |  | Fibre optic multimode |  |  |  | input B --> T | NA | NA | 2000
EB3 |  | Al Invest | Bültmann cameras to AIB monitor | NA | 48 |  | Patch cable |  |  |  | input B --> T | 61075 | 18750 | 1500
EH3 |  | Al Invest | HPI cameras to AIB monitor | NA | 48 |  | Patch cable |  |  |  | input B --> T | 98136 | 26194 | 1500
EH4 |  | Al Invest | Communication line PN/PN coupler to water system | NA | 48 |  | Patch cable |  |  |  | input B --> T | 72362 | 7958 | 800
EH5 |  | Al Invest | Power supply PN/PN coupler from water system |  | 24 |  | 3G4 |  |  |  | input B --> T | 72362 | 7958 | 800
EH6 |  | Al Invest | Communication Sybas | NA | 48 |  | Patch cable |  |  |  | input B --> T | 72362 | 7958 | 500
EH7 |  | Al Invest | Power supply PN/PN coupler to Insertec furnace |  | 24 |  | 3G4 |  |  |  | input B --> T | 82762 | 7958 | 500
EH8 |  | Al Invest | Communication line PN/PN coupler to Insertec furnace | NA | NA |  | Fibre optic multi mode |  |  |  | input B --> T | 82762 | 7958 | 500
EH9 |  | Al Invest | Communication line PN/PN coupler to Insertec furnace | NA | NA |  | Fibre optic multi mode |  |  |  | input B --> T | 82762 | 7958 | 500 | 2nd line for redundancy
EH10 |  | Al Invest | Communication line overall HMI | NA | NA |  | Fibre optic multi mode |  |  |  | input B --> T | 72362 | 7958 | 800
EH11 |  | Al Invest | Internet communication Remote access | NA | NA |  | NA |  |  |  | input B --> T | 72362 | 7958 | 800
|  |  | Total | 1800 |  |  |  |  | (all solidly grounded wye)
TOP compressed air
No | AIB No. | (Sub) Supplier(s) | Description | Requirement | [10 empty] | Remark
|  |  |  | Qair [Nm³/h] | p [bar] |  |  |  | Quality | Connector / Flange | Connection by | X [mm] (from Ref. point AIB) | Y [mm] (from Ref. point AIB) | Z [mm] (from shop floor +-0)
C1 | 107H02 | HPI | Casting line | 1 - 105 | 5-6 |  |  |  | ISO 8573-1:2010 [1.4.1] | G1" | input T --> B | 89866 | 28339 | 1000
C2 | 103H01 | Dynamic Concept | Filterbox Dynaprime | 5 - 405 | 5-6 |  |  |  | ISO 8573-1:2010 [1.4.1] | G1 1/2" | input T --> B | 101866 | 28339 | 1000 | quality: ISO 8573-1:2010 [6.3.3] is sufficient as well Qair only necessary for around 15 sec. / every 2 hours - priming Qair: 5250 Nl/min = 1090 l/min @ 4,8bar (for 15 sec. / every 2 hours)
C3 |  | Pyrotek | Degasser SNIF | 30 | 5-6 |  |  |  | ISO 8573-1:2010 [1.4.1] | G3/4" | input B --> T |  |  |  | TOP merged together with C1
C4 |  | HPI | Casting machine | 5 | 5-6 |  |  |  | ISO 8573-1:2010 [1.4.1] | G3/4" | input B --> T
C6 | 107H03 | ARP | Chips central (seperator + double switch) | 20 - 235 | 5-6 |  |  |  | ISO 8573-1:2010 [3.4.3] | G3/4" | input T --> B | 95766 | 7610 | 1000 | desired pressure 6-8bar
C7 | 103H02 | Bültmann | Testing and Peeling | 20 - 65 | 5-6 |  |  |  | ISO 8573-1:2010 [3.2.3] | G1 1/2" | input B --> T | 71825 | 22600 | 1000
C8 | 103H04 | ARP | suction point: flying saw | 2 - 8 | 5-6 |  |  |  | ISO 8573-1:2010 [7.4.4] | G1/2" | input T --> B | 89866 | 7750 | 1000 | desired pressure 6-8bar
C9 | 103H05 | ARP | suction point: uncontrolled ends | 2 - 8 | 5-6 |  |  |  | ISO 8573-1:2010 [7.4.4] | G1/2" | input T --> B | 41666 | 7750 | 1000 | desired pressure 6-8bar
C10 |  | ARP | suction point: peeling machine | 2 - 8 | 5-6 |  |  |  | ISO 8573-1:2010 [7.4.4] | G1/2" | input T --> B | 65666 | 7750 | 1000 | desired pressure 6-8bar
C11 |  | Bültmann | Packing | 20 - 40 | 5-6 |  |  |  | ISO 8573-1:2010 [3.2.3] | G1 1/2" | input B --> T | 35575 | 16400 | 1000
C91 |  | Al Invest | Mouldshop | 1-50 | 3-5 |  |  |  | ISO 8573-1:2010 [7.4.4] | G3/4" | input T --> B | 53766 | 27909 | 1500 | HPI suggestion for TOP's C91 - C93: installing on each point compressed air hose reel hose length ~10m incl. compressed air quick coupling
C92 |  | Al Invest | Mouldshop | 1-50 | 3-5 |  |  |  | ISO 8573-1:2010 [7.4.4] | G3/4" | input T --> B | 53766 | 29069 | 1500
C93 |  | Al Invest | Mouldshop | 1-50 | 3-5 |  |  |  | ISO 8573-1:2010 [7.4.4] | G3/4" | input T --> B | 41880 | 28489 | 1500
|  |  | Total (consumption corrected for operation mode) | max. ~740
TOP water
No | AIB No. | (Sub) Supplier(s) | Description | Requirement | [10 empty] | Remark
|  |  |  | Qwater [m³/h] | p [bar] |  |  |  | T [°C] Requirement | Connector / Flange | Connection by | X [mm] (from Ref. point AIB) | Y [mm] (from Ref. point AIB) | Z [mm] (from shop floor +-0)
W1 | 220H01 | HPI | Cooling water casting (preflow) | 30 - 100 | 2,5 - 5 |  |  |  | 20–30 °C | DN 100 / PN 16 EN1091-1 - 1.4571 | input B --> T | 92710 | 15700 | -200 | for more details: PID 390-14-00-01-REV-C cooling water pipelines out of stainless steel steady state casting: ~10-20 ltr/h more preflow than backflow because of evaporation (refilling at water plant)
W2 | 221H01 | HPI | Cooling water casting return (+organics) | 30 - 100 | / |  |  |  |  | DN 300 (min.) | free backflow | 95755 | 17800 | -700 | heat load approx 1400 kW out of cooling water casting steady state casting: ~ +15°C of return water in contrast to preflow organics: oil content in water (of casting) 0,8 - 1,2 ltr/h
W3 | 222H01 | HPI | Emergency water casting (preflow) |  | min. 2 |  |  |  | 20–30 °C | DN 65 / PN 16 EN101-1 - 1.4571 | input B --> T | 92710 | 15950 | -200 | Volume of 10m³ must be available
W4 | 223H01 | Bültmann | Fresh water emulsion | [6 empty] | G 3/4" | input B --> T | 67825 | 24700 | 300 | for refilling of emulsion
W5 | 224H01 | Bültmann | Cooling water emulsion | 0 or 3 | 3 |  |  |  | 20–25 °C | G 1 1/2" | input B --> T | 68225 | 24700 | 300 | heat load approx 35 kW / static pressure
W6 | 225H01 | Bültmann | Cooling water emulsion - return | 0 or 3 | 2.5 |  |  |  |  | G 1 1/2" | input B --> T | 68025 | 24700 | 300
W7 | 226H01 | KarlDeutsch | Fresh water coupling agent | 0 - 2 | 2 - 2,5 |  |  |  | 20–35 °C | G 3/4" | input B --> T | 51100 | 16250 | 300 | hardness: max. 18° dH pH: 7,0 to 8,0 filter grade: max. 50ppm unsolved / max. 50µm
W7D | 223H02 | KarlDeutsch | Coupling agent drainage | 0 - 2 | free |  |  |  |  | G 1 " | free backflow | 51100 | 16450 | 300
W8 | 224H02 | Bültmann | Cooling water hydraulic | 0 or 3 | 3 |  |  |  | 20–25 °C | G 1 1/2" | input B --> T | 75175 | 24300 | 300 | heat load approx 11 kW / static pressure
W9 | 225H02 | Bültmann | Cooling water hydraulic - return | 0 or 3 | 2.5 |  |  |  |  | G 1 1/2" | input B --> T | 75175 | 24100 | 300
W10 | 224H03 | Bültmann | Cooling water main gear box | 0 or 1,2 | 3 |  |  |  | 20–25 °C | G 1 " | input B --> T | 62275 | 24500 | 300 | heat load 5 kW / static pressure
W11 | 225H03 | Bültmann | Cooling water main gear box - return | 0 or 1,2 | 2.5 |  |  |  |  | G 1 " | input B --> T | 62275 | 24300 | 300
|  | ARP | flushing centrifuge | 1.8 |  |  |  |  | <25 | G 3/4 |  |  |  |  | Emulsion supplied by Bültmann filter unit
|  | ARP | excess emulsion - return | 2.4 |  |  |  |  | <25 | G 3/4 |  |  |  |  | Emulsion return to Bültmann filter unit
W90 |  | Al Invest | general water mouldshop | 0 - 5 | 2 - 3 |  |  |  |  | sugg. G 3/4" | input B --> T | 57610 | 24766 | 500
W91 |  | Al Invest | general water mouldshop return | 0 - 5 | 2 - 3 |  |  |  |  | sugg. G 1" | input B --> T | 57640 | 24766 | 500
TOP natural gas
No | AIB No. | (Sub) Supplier(s) | Description | Requirement | [10 empty] | Remark
|  |  |  | Qngas [Nm³/h] | p [mbar] |  |  |  |  | Connector / Flange | Connection by | X [mm] (from Ref. point AIB) | Y [mm] (from Ref. point AIB) | Z [mm] (from shop floor +-0)
G1 | 302H01 | Promeos | Tundish preheating | 8 - 10 | 30 - 60 |  |  |  |  | G 3/4" | input S --> N | 86981 | 12883 | -525 | gas pressure at TOP point from 1bar will be reduced to 30-60mbar on the pressure regulation line
G2 | 302H02 | Dynamic Concept | Filterbox Dynaprime | 0 - 16 | 150-200 |  |  |  |  | G 1" | input T --> B | 101866 | 28239 | 1000 | 7,5 Nm³/h for each filterbox preheating unit 280.000 BTU/h --> 80kW gas pressure at TOP point from 1bar will be reduced to 150-200mbar on the gas pressure regulation line
TOP exhaust gas
No | AIB No. | (Sub) Supplier(s) | Description | Requirement | [10 empty] | Remark
|  |  |  | Qngas [Nm³/h] | T [°C] |  |  |  |  | Connector / Flange | Connection by | X [mm] (from Ref. point AIB) | Y [mm] (from Ref. point AIB) | Z [mm] (from shop floor +-0)
X1 | 810H01 | Pyrotek | Degasser SNIF | 680 - 850 | 50-80 |  |  |  |  | DN 100 - 1.4301 inner-Ø= 108,5mm out-Ø= 230mm holes-Ø= 190,5mm hole-Ø= 19mm n-holes= 8 | input B --> T | 102177 | 27829 | 7425 | Composition of exhaust air: depends on lot of factors (ambient air + process gas mix / amount) composition: max. 10Nm³/h of process gas (Ar) + traces of HCL (depending on degassing process) + ambient air temperature of exhaust gas: depending mostly on ambient air temp. (main part of the exhaust gas) .. max. 120°C static pressure increase: 5000-6000 Pa suggested piping material: 1.4301 /// AISI SAE 304
X2 |  | Pyrotek | Degasser flushing (for pipe cleaning of Cl) | <6 | free |  |  |  |  | G 1/4" | input T --> B |  |  |  | Return gas from flushing (Cl contaminated)
X3 | 811H01 | Scheuch | Chip suction (flying saw) exhaust | 5070 | 10-40 |  |  |  |  | DIN 24154/R4 NW 0250 | no connection free blowing out input W --> E | 92017 | 10167 | 5400 | TOP flange located in a height of ~4900mm above floor incl. 90° bow for free blow out into hall total pressure increase: 11.312Pa static pressure increase: 10.844Pa sound pressure level at TOP: 45-50dB(A)
X4 |  | ARP | Chip suction (central) vacuum compressor | 1200 - 1500 | 20-50 |  |  |  |  | out-Ø 114,3 | no connection free blowing out input B --> T | 96550 | 9422 | 1360 | will be blown out diffusely into hall incl. Installed silencer
X5 |  | Bültmann | Filter unit peeling machine | 5000 - 6000 | 40-50 |  |  |  |  | - | no connection free blowing out input B --> T | 61537 | 26063 | 2000
TOP technical gas
No | AIB No. | (Sub) Supplier(s) | Description | Requirement | [10 empty] | Remark
|  |  |  | Qngas [Nm³/h] | p [bar] |  |  | Pipe size |  | Connector / Flange | Connection by | X [mm] (from Ref. point AIB) | Y [mm] (from Ref. point AIB) | Z [mm] (from shop floor +-0)
A1 | 451H01 | Pyrotek | SNIF Degasser Cl | 0 - 0,46 | 1,9 - 2,1 |  |  |  |  | 1/4" | input B --> T | t.b.def. (positioned in gas mixingroom) | t.b.def. (positioned in gas mixingroom) | t.b.def. (positioned in gas mixingroom) | Chlorine Purity: 99.5% high purity grade chlorine with less than 100 ppm of moisture (a dew point of less than -44°F or -42°C) with a minimum check temperature of 40°F (4.5°C)
A2 | 401H01 | Pyrotek | SNIF Degasser Argon | 0 - 9,0 | 4,8 - 5,0 |  |  | up to customer suggestion: 3/4" |  | 1/2" - NPT | input B --> T | t.b.def. (positioned in gas mixingroom) | t.b.def. (positioned in gas mixingroom) | t.b.def. (positioned in gas mixingroom) | Argon (4.0 or 4.6) Purity: 99.996% pure with less than 3 ppm of moisture (a dew point of less than -92°F or -69°C) and less than 5 ppm of oxygen max. 10bar of supply pressure at TOP Argon pressure at TOP (12bar) will be reduced to working pressure (Swagelok pressure reducer will be supplied by HPI - installation by AIB - thread connection pressure reducer 1/2" NPT female)
A3 |  | Pyrotek | SNIF Degasser Argon (auxiliary) | 0 - 0,5 | 1,9 - 2,2 |  |  | up to customer suggestion: 1/2" or 3/4" |  | 1/2" - NPT | input B --> T | t.b.def. (positioned in gas mixingroom) | t.b.def. (positioned in gas mixingroom) | t.b.def. (positioned in gas mixingroom) | Argon (4.0 or 4.6) Purity: 99.996% pure with less than 3 ppm of moisture (a dew point of less than -92°F or -69°C) and less than 5 ppm of oxygen max. 7bar of supply pressure at TOP (Swagelok pressure reducer will be supplied by HPI - installation by AIB - thread connection pressure reducer 1/4" NPT female)
A4 |  | Pyrotek | Chlorine relief vent |  | free |  |  |  |  | 1/4" | input B --> T | t.b.def. (positioned in gas mixingroom) | t.b.def. (positioned in gas mixingroom) | t.b.def. (positioned in gas mixingroom) | outlet of chlorine relief valve must be vented, in accordance to country national safety codes
A10 | 461H01 | AIB | SNIF process gas line entry point- for nozzle (rotor) | 0 - 9,0 | 1,3 - 1,5 |  |  | up to customer suggestion: 3/4" pipe size / pipe routing: must be designed to have not more than 0,3bar pressure loss at 14 Nm³/h gas flow at 0,4bar line exit pressure (at A11) before connecting to equipment - blown with dry nitrogen + pressure check - by AIB suggested fitting system: Swagelok SST316 |  | 1/2" - NPT | input B --> T | t.b.def. (positioned in gas mixingroom) | t.b.def. (positioned in gas mixingroom) | t.b.def. (positioned in gas mixingroom) | connection point in gas mixing room for process gas line to plant - to A11 (leak test before installation works by AIB) material of pipeline: according to national standards suggestion: stainless steel A4 (1.4571)
A11 | 462H01 |  | SNIF process gas line exit point- for nozzle (rotor) | [6 empty] | 1/2" - NPT | input N --> S | 98086 | 25089 | -525 | connection point at plant for process gas line - from A10 (leak test before installation works by AIB) material of pipeline: according to national standards suggestion: stainless steel A4 (1.4571)
A20 |  | AIB | SNIF process gas line entry point- for nozzle idle | 0 - 1,1 | 0,6 - 0,8 |  |  | up to customer suggestion: 1/2" pipe size / pipe routing: must be designed to have not more than 0,3bar pressure loss at 14 Nm³/h gas flow at 0,4bar line exit pressure (at A21) before connecting to equipment - blown with dry nitrogen + pressure check - by AIB suggested fitting system: Swagelok SST316 |  | 1/2" - NPT | input B --> T | t.b.def. (positioned in gas mixingroom) | t.b.def. (positioned in gas mixingroom) | t.b.def. (positioned in gas mixingroom) | connection point in gas mixing room for process gas line to plant - to A21 (leak test before installation works by AIB) material of pipeline: according to national standards suggestion: stainless steel A4 (1.4571)
A21 |  |  | SNIF process gas line exit point- for nozzle idle | [6 empty] | 1/2" - NPT | input N --> S | 98086 | 25139 | -475 | connection point at plant for process gas line - from A20 (leak test before installation works by AIB) material of pipeline: according to national standards suggestion: stainless steel A4 (1.4571)
Note on A6: Christoph Zimmerbauer: Electric supply HPI
Note on A16: Christoph Zimmerbauer: Electrical supply Bültmann
Note on A38: Christoph Zimmerbauer: 230 VAC supply for HPIs lights and sockets
Note on A39: Christoph Zimmerbauer: 230 VAC supply for lights and sockets of Bültmann