## Tabelle1
Bloom Ref no.. | 60309
Quotation no. | BEU22400233_rev.9
Customer | Insertec
PID no. | 1-60309-00
Date | 16.07.2025 |  |  | Valve and Equipment-List |  |  |  | Spare parts refer to 6 combustion systems
Revision no. | 2
Manufacturer | PID no. | Bloom- Article no. | Pcs | Description | Type | DN | Scope of supply | Spare parts for commissioning | Spare parts for 2 year operation
Natural gas
Elster Kromschröder | 670 | P-15000-00050-0066 | 1 | Ball valve DN 80 For manual operation in gas, air, water and oil. pe max: 16 bar enviromental temp. -20°C to +60°C EG approval and certificate | AKT 80F160C | 80 | Bloom
Elster Kromschröder | 870 | P-15000-00006-0001 | 6 | for manual operation in gas, air , water and oil Rp thread ; pe max 5bar enviromental temp. -20°C to +60°C | AKT 6R50B | R1/4" | Bloom
Elster Kromschröder | 680 | P-11000-00050-0019 | 1 | Gasfilter with filter in Polypropylen, for cleaning of gas and air EG certificate DN 80 Flange connection acc. to ISO 7005 max. pressure 4 bar sample plug at the inlet and outlet | GFK 80F40-6 | 80 | Bloom | 2 x spare parts set for GFK 80 (includes filter inlay and o-ring sealing) | 2 x spare parts set for GFK 80 (includes filter inlay and o-ring sealing)
Elster Kromschröder | 690 | P-18000- | 1 | pressure gauge 0 - 1,6 bar for gas and air ; male threaded; brass + stainless steel ; 100mm skale diameter with zero point adjustment | RFM 1,6RB100 | R 1/2" | Bloom | 2 | 2
Elster Kromschröder | 700 | P-19000-00000-0001 | 1 | Pressure gauge cock 1/2" for gas and air with certificate Thread connection (female) pe max. 5 bar | MH 15 | R 1/2" | Bloom
Elster Kromschröder | 705 | P- | 1 | flow meter for gas gas: V = 401 Nm3/h, Pmax= 1,2 bar,installed betwen flange | DM160Z80-40 | 80 | Bloom |  | 1
| 706 |  | 1 | Safety shut-off valve For safeguarding all controls connected downstream of a gas pressure regulator, EU certified Nominal diameter: DN 50 Pipe connection: Flange to ISO 7005 Inlet pressure: pu max. 5 bar Monitoring: Over-pressure shut-off pdo (yellow spring 200-350mbar) OPSO | JSAV50R40 /1-3 | 50 | Bloom | 1 x gasket set | 2 x gasket set
Elster Kromschröder | 710 | P-07100- | 1 | pressure regulator for gas spring reacting with adjusted pressure range for constant pressure outlet EG certified spring rang: 220-350 mbar | VGBF 50F40-3 | 50 | Bloom | 1 x spare part pack | 2 x spare part pack
Elster Kromschröder | 730 | P-24100-00025-0003 | 1 | safety relief valve Rp thread female max inlet pressure 4 bar, Spring: 165-330 mbar measurment nozzle at inlet range according spring | VSBV 25R40-4 | 1" | Bloom | 1 x spare part pack | 2 x spare part pack
Elster Kromschröder | 740 | P-18000-00000-0006 | 1 | Pressure gauge 0 - 400 mbar for gas and air male threaded stainless steel 100 mm scale diameter with zero point adjustment | KFM 400RB100 | 1/2" | Bloom | 1 | 2
Elster Kromschröder | 750 | P-19000-00015-0002 | 1 | Pressure gauge cock 1/2" for gas and air with certificate. Rp thread / female / male pemax. 100 bar | DH 15R50 | R 1/2" | Bloom
Elster Kromschröder | 760 | P-08000-00150-0014 | 2 | pressure switch range 30 - 150 mbar , overpressure , vaccuum and differential pressure el. connection with screw terminal manual adjustment of set point EG certificate | DG 150U-3 |  | Bloom | 1 | 3
Elster Kromschröder | 770 | P-08000-00500-0007 | 2 | pressure switch, range 100 - 500 mbar , overpressure , vaccuum and differential pressure golden contacts , el. connection with screw terminal manual adjustment of set point EG certificate | DG 500UG-3 |  | Bloom | 1 | 3
Elster Kromschröder | 860 | P-15000-00080-0078 | 1 | ball valve for manual operation in gas, air , water and oil Rp thread ; pe max 16 bar temp. -20°C to +60°C EG approval and certificate | AKT 80F160C | 80 | Bloom
Elster Kromschröder | 780 | P-17000-00080-0058 | 1 | solenoid valv class A EN161, powerless closed, for gas and air, incl. control LED, IP65, EG certificate, flanges according ISO 7005, max. inlet pressure 500 mbar (7psig) fast opening , fast closing electrical connection M20, 230 VAC 50Hz, 24 VDC limit switch measurement plug in- and outlet | VAS 780F05NWGR3M/PP/PP | 80 | Bloom | 1 | 2
Dungs | 790 | P-04000-00000-0014 | 1 | tightness control VPM-VC V1.1 | VPM-VC 1.1 / 301 234 |  | Bloom | 1 | 2
Elster Kromschröder | 800 | P-17000-00025-0083 | 1 | gas solenoid valve fast opening fast closing flow adjustment availabale,class A acc En161 powerless closed for gas and air maximum pressure 500mbar incl. control LED, IP65 EG certificate, RP connection female power 230 VAC 50Hz, electrical connection M20 | VAS 125R/NW | 1" | Bloom | 1 | 2
Elster Kromschröder | 805 | P-08000-00150-0014 | 1 | pressure switch range 30 - 150 mbar , overpressure , vaccuum and differential pressure el. connection with screw terminal manual adjustment of set point EG certificate | DG 150U-3 |  | Bloom
Siemens | 785 |  | 2 | Temperature sensor Sitrans TS500, range -50 - 400°C, calibrated -20 - 100°C, depth 100mm | 7MC7512-1CA01-1AA1-Z C20+E00+T34+Y01 |  | Bloom | 1 | 2
Siemens | 795 | P-05000-00000-0043 | 2 | Pressure transmitter Sitrans P320, range 1000 mbar | 7MF0300-1JD01-5AF2-Z A00+C20+E00 |  | Bloom | 1 | 2
Elster Kromschröder | 145 | P-08000-00150-0014 | 1 | pressure switch range 30 - 150 mbar , overpressure , vaccuum and differential pressure el. connection with screw terminal manual adjustment of set point EG certificate | DG 150U-3 |  | Bloom
| 835 |  | 1 | Flexible DN80, length : 1.600 mm connection one side fixed flange one side loose flange with DVGW, BY OTHERS |  | 80 | Insertec
Siemens | 820 |  | 2 | SITRANS P320 Pressure transmitter Differential pressure and flow PN160 HART (4...20 mA) Measuring cell filling: Silicone oil Maximum measuring span: 20 mbar (24.11 inH²O) Oval flange, fastening thread: M10 (PN160), M12 (PN420) Diaphragm: Stainless steel 316L/1.4404, measuring cell: Stainless steel 316L/1.4404; Sensor Differential pressure no Ex 2 x M20 x 1.5 With display (lid with glass window) Functional Safety (IEC 61508) - SIL2/3; Electrical equipment for furnaces and ancillary equipment (EN 50156-2) General approval without Ex approval: World (CE, RCM) except: EAC, FM, CSA, KCC | Sitrans P320 7MF0340-1BM01-5AF2-Z C20+E00 |  | Bloom | 1 | 2
Schneider | 825 | P-01050-00015-0001 | 2 | 3 valve manifold NPT for direct connection to transmitter. Connections: Inlet: 1/2" NPT female Outlet: DIN EN 61518; Type A | N542.39.481.01 | 1/2" NPT | Bloom
Elster Kromschröder | 815 | P-15000-00006-0001 | 4 | Ball valve 1/4" for manual operation in gas, air , water and oil Rp thread ; pe max 5 bar enviromental temp. -20°C to +60°C EG approval and certificate | AKT 6R50B | R 1/4" | Bloom
Dosch | 810 |  |  | annular chamber orifice assembly: for installation between 2 flanges Differential pressure: 15 mbar, DN80, 4 connections 1/4" Vgas=401 Nm3/h, Pe=230 mbar |  | 80 | Bloom
Jasta | 830 | P- | 1 | Control butterfly valve for installation between 2 flanges DN 50 PN 10 for natural gas JASTA GD6, DVWG cert. complete assembled with pneumatic actuator, open/close 3 - 5 seconds max., and Siemens SIPART PS 2, Type: 6DR5010-0NG01-0AA0-Z C20, 4-20 mA in- and output, 24VDC |  | 50 | Bloom | 1 x pneumatic actuator, 1 x Sipart PS 2 | 1 x pneumatic actuator, 1 x Sipart PS 2
Elster Kromschröder | 890 | P-15000-00080-0078 | 2 | ball valve for manual operation in gas, air , water and oil Rp thread ; pe max 16 bar enviromental temp. -20°C to +60°C EG approval and certificate | AKT 80F160C | 80 | Bloom
Elster Kromschröder | 900+910 | P-17250-00080-0011 | 2 | double shut off valve 230 VAC , as gas safety shut off valve acc EN161 class A 1st valve fast open / fast close, 2nd valve slow open / fast close flow adjustable Solenoid actuator 230 VAC 50/60 Hz, 24 VDC limit switch electrical connection M20 max operation pressure 500 mbar IP 65 EG certificate | VCS780F05NLWGR3/PPPP/PPPP | 80 | Bloom | 1 | 3
Elster Kromschröder | 915 | P-04000-00000-0017 | 2 | Tightness controls for checking two safety valves before or after burner run, with adjustable test period or measurement time for adjustment to different test volumes, leakage rates and inlet pressures, EC type-tested and certified. TC 3 for quick or slow opening individual valves, pu: max. 500 mbar, voltage: 24 V= | TC 3R05K/K | 1/4" | Bloom | 1 | 3
Uni Geräte | 930 | P-12000-00080-0008 | 2 | control valve, manual adjustment Regulating ratio 10:1 EC type examination certificate for medium temperature range -20°C bis +60°C Intermediate flange flap | MRK Ro HA 30N-4.00.32 | 80 | Bloom
Elster Kromschröder | 920 | P-14300-00080-0006 | 2 | Compensator DN 80 for gas, air and water, pe max. 10 bar Execution with loose flanges drilled according to DIN 2501 PN 10 DIN-DVGW tested and registered Operating temperature - for air: -20°C bis +500°C - for gas: -20 bis + 150°C - for water: 0° bis + 100°C | EKO 80F | 80 | Bloom |  | 1
Second Stage Air
Reitz | 270 | P- | 1 | REITZ Combustion Air Fan Air Flow: 4.350 Nm³/h Total pressure 100 mbar Motor Make Innomotics: IE4 37 kW / 50Hz / 400 VD / IP55 / 2955 min-1 3 PTC Thermistor / 1 PT100 / incl. filter, compensator for outlet and vibration damper / Position outlet: tbd |  |  | Insertec
Elster Kromschröder | 280 | P-18000-00000-0002 | 1 | pressure gauge 0 - 160 mbar for gas and air ; male threaded, brass ; 100mm skale diameter ; with zero point adjustment | KFM 160RB100 | 1/2" | Bloom | 1 | 2
Elster Kromschröder | 290 | P-19000-00015-0002 | 1 | Pressure gauge cock 1/2" for gas and air with certificate. Rp thread / female / male pemax. 100 bar | DH 15R50 | R 1/2" | Bloom
Elster Kromschröder | 300 | P-08000-00050-0004 | 2 | Pressure switch range 2,5 - 50 mbar , overpressure , vaccuum and differential pressure golden contacts , el. connection with screw terminal manual adjustment of set point EG certificate | DG 50UG-3 |  | Bloom | 1 | 3
Siemens | 295 |  | 2 | Temperature sensor Sitrans TS500, range -50 - 400°C, calibrated -20 - 100°C, depth 180mm | 7MC7512-1CA05-1AA1-Z C20+E00+T34+Y01 |  | Bloom
Siemens | 305 | P-05000-00000-0043 | 2 | Pressure transmitter Sitrans P320, range 250 mbar | 7MF0300-1FD01-5AF2-Z A00+C20+E00 |  | Bloom
| 310 |  | 1 | Measuring orifice for air, installation between flanges DN350, V= 5200 Nm3/h, Pe= 90 mbar, differential pressure : 15 mbar |  | 350 | Bloom
Schneider | 375 | P-01050-00015-0001 | 2 | 3 valve manifold NPT for direct connection to transmitter. Connections: Inlet: 1/2" NPT female Outlet: DIN EN 61518; Type A | N542.39.481.01 | 1/2" NPT | Bloom
Siemens | 370 |  | 2 | SITRANS P320 Pressure transmitter Differential pressure and flow PN160 HART (4...20 mA) Measuring cell filling: Silicone oil Maximum measuring span: 20 mbar (24.11 inH²O) Oval flange, fastening thread: M10 (PN160), M12 (PN420) Diaphragm: Stainless steel 316L/1.4404, measuring cell: Stainless steel 316L/1.4404; Sensor Differential pressure no Ex 2 x M20 x 1.5 With display (lid with glass window) Functional Safety (IEC 61508) - SIL2/3; Electrical equipment for furnaces and ancillary equipment (EN 50156-2) General approval without Ex approval: World (CE, RCM) except: EAC, FM, CSA, KCC | Sitrans P320 7MF0340-1BM01-5AF2-Z C20+E00 |  | Bloom
Jasta | 340 | P- | 1 | Control butterfly valve for installation between 2 flanges DN 200 PN 10 for air and natural gas JASTA GD6, DVWG cert. complete assembled with pneumatic actuator, open/close in 3 - 5 seconds max., and Siemens SIPART PS 2, Type: 6DR5010-0NG01-0AA0-Z C20, 4-20 mA in- and output, 24VDC |  | 200 | Bloom | 1 x pneumatic actuator, 1 x Sipart PS 2 | 1 x pneumatic actuator, 1 x Sipart PS 2
Jasta | 350 |  | 2 | Butterfly valve for installation between 2 flanges DN 350 PN 10 for air, with handle |  | 350 | Bloom
Jasta | 380 |  | 2 | Butterfly valve for installation between 2 flanges DN350, incl. step seat sealing,for air / waste gas 450°C, with pneumatic actuator, single-acting, open/close in 1 second 5 bar compressed air with 3/2-way solenoid valve 24VDC leakage approx. 0,02% of kv 90°, PN 10, incl. Position switch 24VDC open/close, 2-wire |  | 350 | Bloom | 1 x 3/2-way solenoid valve | 2 x 3/2-way solenoid valve
IBK | 410 |  | 2 | special execution; max. operating temp.: up to 350°C total length: 265 mm extensibility:ax. 23 mm / lat. 9 mm ; PN10 |  | 350 | Bloom
| 1100 |  | 1 | Flexible DN350, length : XXX mm connection one side fixed flange one side loose flange with DVGW, BY OTHERS |  | 350 | Insertec
First Stage Air
Dosch | 420 | P- |  | Measuring orifice for air, installation between flanges DN150, V= 844 Nm3/h, Pe= 90 mbar, differential pressure : 15 mbar |  | 150 | Bloom
Siemens | 430 |  | 1 | SITRANS P320 Pressure transmitter Differential pressure and flow PN160 HART (4...20 mA) Measuring cell filling: Silicone oil Maximum measuring span: 20 mbar (24.11 inH²O) Oval flange, fastening thread: M10 (PN160), M12 (PN420) Diaphragm: Stainless steel 316L/1.4404, measuring cell: Stainless steel 316L/1.4404; Sensor Differential pressure no Ex 2 x M20 x 1.5 With display (lid with glass window) Functional Safety (IEC 61508) - SIL2/3; Electrical equipment for furnaces and ancillary equipment (EN 50156-2) General approval without Ex approval: World (CE, RCM) except: EAC, FM, CSA, KCC | Sitrans P320 7MF0340-1BM01-5AF2-Z C20+E00 |  | Bloom | 1 | 1
Schneider | 435 | P-01050-00015-0001 | 1 | 3 valve manifold NPT for direct connection to transmitter. Connections: Inlet: 1/2" NPT female Outlet: DIN EN 61518; Type A | N542.39.481.01 | 1/2" NPT | Bloom
Jasta | 450 | P- | 1 | Control butterfly valve for installation between 2 flanges DN 100 PN 10 for air JASTA GD6, complete assembled with pneumatic actuator, open/close in 3 - 5 seconds max., and Siemens SIPART PS 2, Type: 6DR5010-0NG01-0AA0-Z C20, 4-20 mA in- and output, 24VDC |  | 100 | Bloom | 1 x pneumatic actuator, 1 x Sipart PS 2 | 1 x pneumatic actuator, 1 x Sipart PS 2
Jasta | 460 | P- | 2 | Butterfly valve for installation between 2 flanges DN 150 PN 10 for air, with handle |  | 150 | Bloom
Jasta | 490 | P- | 2 | Butterfly valve for installation between 2 flanges DN150, incl. step seat sealing,for air, with pneumatic actuator, single-acting, open/close in 1 second 5 bar compressed air with 3/2-way solenoid valve 24VDC leakage approx. 0,02% of kv 90°, PN 10, incl. Position switch 24VDC open/close, 2-wire |  | 150 | Bloom
Kromschröder | 530 | P- | 2 | execution with loose flanges; operating temp.: -20°C to +250°C total length: 175 mm extensibility: ax. 22mm / lat. 4,1mm, PN10 | EKO 150F | 150 | Bloom
Pilot and Cooling Air
Reitz | 540 |  | 1 | REITZ Pilot and Cooling Air Fan Air Flow: 1200 Nm³/h Total pressure 80 mbar Motor Make Innomotics: IE4 18.5 kW / 50Hz / 400 VD / IP55 / 2955 min-1 3 PTC Thermistor / 1 PT100 / incl. filter, compensator for outlet and vibration damper / Position outlet: tbd |  |  | Insertec
Elster Kromschröder | 550 | P-18000-00000-0001 | 1 | Pressure gauge ; 0 - 100 mbar for gas and air ; male threaded; brass + stainless steel; 100 mm scale diameter; with zero point adjustment | KFM 100RB100 | 1/2" | Bloom | 1 | 2
Elster Kromschröder | 555 | P-19000-00015-0002 | 1 | Pressure gauge cock 1/2" for gas and air with certificate Thread connection (female) pe max. 5 bar | DH 15R50 | R 1/2" | Bloom
Elster Kromschröder | 570 | P-08000-00050-0004 | 2 | Pressure switch, range 2,5 - 50 mbar , overpressure , vaccuum and differential pressure golden contacts , el. connection with screw terminal, manual adjustment of set point EG certificate | DG 50UG-3 | 1/4" | Bloom | 1 | 1
Elster Kromschröder | 571 |  | 1 | Adjusting cock 1 1/2" thread design; adjustment with tools max operation pressure gas 4 bar ; max. operation pressure air 4 bar | LEH 40R40 | 1 1/2" | Bloom
| 572 |  | 1 | Measuring orifice for air, installation between flanges DN40, V= 70 Nm3/h, Pe= 80 mbar, differential pressure : 15 mbar |  | DN40 | Bloom
Elster Kromschröder | 573 | P-08000-00050-0004 | 1 | Pressure switch, range 2,5 - 50 mbar , overpressure , vaccuum and differential pressure golden contacts , el. connection with screw terminal, manual adjustment of set point EG certificate | DG 50UG-3 | 1/4" | Bloom
Elster Kromschröder | 260 | P-10000-00015-0010 | 2 | Adjusting cock 1/2" thread design; adjustment with tools max operation pressure gas 1 bar ; max. operation pressure air 4 bar | GEH 15R10 | R 1/2" | Bloom
IBK | 225 | P-23310-00000-0006 | 2 | Flexible hose 1/2" length 500 mm connection one side male thread one side threaded joint DVGW certificate | ES15RA500 | 15 / 1/2" | Bloom
Elster Kromschröder | 80 | P-07000-00025-0041 | 2 | pressure regulator outlet pressure : 25 - 75 mbar spring reacting; for constant pressure for Gas; measuring control nozzle in the inlet EG certificate pe max 400 mbar | GDJ 25R04-4Z | 1" | Bloom | 1 | 2 x spare part pack
Uni Geräte | 70 | P-10000-00025-0004 | 1 | Adjustment valve 1" thread design ; max operation pressure 10 bar. For air and gas with temp. -20°C up to +60°C |  | Rp 1" | Bloom
Elster Kromschröder | 210 | P-23310-00025-0028 | 2 | Flexible hose 1" length 500 mm connection one side male thread one side threaded joint DVGW certificate | ES25RA500 | 25 / 1" | Bloom
Elster Kromschröder | 510 | P-02100-00050-0014 | 2 | orifice plate assembly incl. taps, completly assembled threaded connection | VMO 250R05M38 | 2 " | Bloom
Elster Kromschröder | 440 | P-08000-00050-0004 | 2 | Pressure switch range 2,5 - 50 mbar , overpressure , vaccuum and differential pressure golden contacts , el. connection with screw terminal manual adjustment of set point EG certificate | DG 50UG-3 | 1/4" | Bloom
Uni Geräte | 520 | P-10000-00050-0007 | 2 | Flow-control-valve thread design ; max operation pressure 10 bar | 10-MEA 20-4 | Rp 2" | Bloom
Elster Kromschröder | 250 | P-10000-00015-0010 | 2 | Adjusting cock 1/2" thread design; adjustment with tools max operation pressure gas 1 bar ; max. operation pressure air 4 bar | GEH 15R10 | R 1/2" | Bloom
IBK | 240 | P-23310-00000-0006 | 2 | Flexible hose 1/2" length 500 mm connection one side male thread one side threaded joint with DVGW certificate | ES15RA500 | 15 / 1/2" | Bloom
Elster Kromschröder | 230 | P-03100-00000-0003 | 2 | UV scanner for intermittently operation in aluminium body with terminal connection IP55 protection. Heat protection by silica glas. Connection: Rp 1/2" | UVS 10D1G1 |  | Bloom | 2 | 4
Gas for Pilot burner
Elster Kromschröder | 190 | P-15000-00015-0009 | 1 | ball valve for manual operation in gas, air , water and oil Rp thread ; pe max 16bar enviromental temp. -20°C to +60°C EG approval and certificate | AKT 15R160S | R 1/2" | Bloom
Elster Kromschröder | 170 | P-18000-00000-0014 | 1 | pressure gauge 0 - 1,6 bar for gas and air ; male threaded; brass + stainless steel ; 100mm skale diameter ; with zero point adjustment | RFM 1,6RB100 | R 1/2" | Bloom | 1 | 2
Elster Kromschröder | 180 | P-19000-00015-0002 | 1 | Pressure gauge cock 1/2" for gas and air Thread connection (female) pe max. 5 bar | DH 15R50 | R 1/2" | Bloom
Fiorentini | 200 |  | 1 | pressure regulator with Integrated safety shut valve ant Integrated safety relief, Intet pressure P = 1,2 bar, outlet pressure P = 20-100 mbar, and flow V = 5,2 Nm3/h | FE6 | 1/2" | Bloom | 1
Elster Kromschröder | 140 | P-08000-00050-0013 | 2 | pressure switch range 2,5 - 50 mbar , overpressure , vaccuum and differential pressure el. connection with screw terminal manual adjustment of set point EG certificate | DG 50U-3 |  | Bloom
Elster Kromschröder | 130 | P-08000-00150-0014 | 2 | pressure switch range 30 - 150 mbar , overpressure , vaccuum and differential pressure el. connection with screw terminal manual adjustment of set point EG certificate | DG 150U-3 |  | Bloom
Elster Kromschröder | 150 | P-18000-00000-0001 | 1 | Pressure gauge ; 0 - 100 mbar for gas and air ; male threaded; brass + stainless steel; 100 mm scale diameter; with zero point adjustment | KFM 100RB100 | 1/2" | Bloom | 1
Elster Kromschröder | 180 | P-19000-00015-0004 | 1 | Pressure gauge cock 1/2" for gas and air Thread connection (female) pe max. 5 bar | DH 15R50 | 1/2" | Bloom
| 87 |  | 1 | Flexible 1/2" x 1000, os. Inner thread, os. Inner thread union |  | 1/2" | Insertec
Elster Kromschröder | 89 |  | 1 | Pressure switch for under pressure (gas/air) range: 2,5 bis 50 mbar tension: 12-250 V golden contacts , el. connection with screw terminal manual adjustment of set point EG certificate | DG 50U-3 |  | Bloom
Elster Kromschröder | 90 | P-15000-00015-0009 | 2 | ball valve for manual operation in gas, air , water and oil Rp thread ; pe max 16 bar enviromental temp. -20°C to +60°C EG approval and certificate | AKT 15R160S | R 1/2" | Bloom
Elster Kromschröder | 95 | P-07000-00025-0041 | 2 | pressure regulator outlet pressure : 25 - 75 mbar spring reacting; for constant pressure for Gas; measuring control nozzle in the inlet EG certificate pe max 400 mbar | GDJ 15R04-4Z | 1/2" | Bloom | 1 | 2 x spare part pack
Elster Kromschröder | 100 | P-17000-01510-0080 | 4 | Solenoid valve 1/2" powerless closed, fast opening, fast closing, for nat. gas, town gas, liquid gas and air . Class A acc EN 161 EG certificate Thread connection pe max. 100 mbar Power supply: 230 V~ 50/60 Hz Low noise operation | VG 15/10R01T6G | 1/2" | Bloom | 1 | 1
Uni Geräte | 60 | P-10000-00015-0002 | 2 | Adjustment valve 1/2" for natural gas and air. thread design max operation pressure 10 bar. For air and gas temp. -20°C up to +60°C | 10-MEA 5-4.01 | Rp 1/2" | Bloom
IBK Wiesehahn | 220 | P-23310-00000-0006 | 2 | Flexible hose 1/2" length 500 mm connection one side male thread one side threaded joint with DVGW certificate |  | 15 / 1/2" | Bloom
Waste Gas
Reitz | 580 |  |  | REITZ Waste Gas Fan Flow: 4500 Nm³/h Total pressure -105 mbar Motor Make Innomotics: IE4 75 kW / 50Hz / 400 VD / IP55 / 2978 min-1 3 PTC Thermistor / 1 PT100 / compensator for in- and outlet and vibration damper / Position outlet: XXX |  |  | Insertec
Elster Kromschröder | 600 | P-08000-00120-0045 | 1 | Pressure switch for under pressure (gas/air) range: -10 bis -120 mbar tension: 12-250 V golden contacts , el. connection with screw terminal manual adjustment of set point EG certificate | DG 120IG-3 | 1/4" | Bloom | 1 | 2
Dittmer | 560 | P-26000-00000-0031 | 3 | Thermocouple Type K 1 x NiCrNi, nominal length = 250 mm Execution with replaceable gauge slide Protection tube ø 10 x 1 mat. 1.4541 Connection head form B with cable connection M 20 x 1,5 | Typr K |  | Bloom | 1 | 2
Eriks | 590 | P-26600-00400-0005 | 1 | Bimetal Thermometer Temperature range 0 - 400°C , Size 100 Connection: G1/2"B Connection type: 4 compression fitting Sensor dia: 8 mm L1= 250 mm | R52.100 | G 1/2" | Bloom
Dosch | 630 | P- |  | Measuring orifice for air, installation between flanges DN350, V= 4150 Nm3/h, Pe= -90 mbar, differential pressure : 15 mbar |  | 350 | Bloom
Siemens | 640 |  | 1 | SITRANS P320 Pressure transmitter Differential pressure and flow PN160 HART (4...20 mA) Measuring cell filling: Silicone oil Maximum measuring span: 20 mbar (24.11 inH²O) Oval flange, fastening thread: M10 (PN160), M12 (PN420) Diaphragm: Stainless steel 316L/1.4404, measuring cell: Stainless steel 316L/1.4404; Sensor Differential pressure no Ex 2 x M20 x 1.5 With display (lid with glass window) Functional Safety (IEC 61508) - SIL2/3; Electrical equipment for furnaces and ancillary equipment (EN 50156-2) General approval without Ex approval: World (CE, RCM) except: EAC, FM, CSA, KCC | Sitrans P320 7MF0340-1BM01-5AF2-Z C20+E00 |  | Bloom
Schneider | 645 | P-01050-00015-0001 | 1 | 3 valve manifold NPT for direct connection to transmitter. Connections: Inlet: 1/2" NPT female Outlet: DIN EN 61518; Type A | N542.39.481.01 | 1/2" NPT | Bloom
Siemens | 625 | P-05000-00000-0043 | 1 | Pressure transmitter Sitrans P320, range 250 mbar | 7MF0300-1FD01-5AF2-Z A00+C20+E00 |  | Bloom
Jasta | 620 | P- | 1 | Control butterfly valve for installation between 2 flanges DN 200 PN 10 for air and gas JASTA GD6,450°C. complete assembled with pneumatic actuator, open/close in 3 - 5 seconds max., and Siemens SIPART PS 2, Type: 6DR5010-0NG01-0AA0-Z C20, 4-20 mA in- and output, 24VDC |  | 200 | Bloom
Jasta | 635 |  | 2 | Butterfly valve for installation between 2 flanges DN 350 PN 10 for gas, 450°C, with handle |  | 350 | Bloom
Jasta | 650 |  | 2 | Butterfly valve for installation between 2 flanges DN350, incl. step seat sealing,for air / waste gas 450°C, with pneumatic actuator, single-acting, open/close in 1 second 5 bar compressed air with 3/2-way solenoid valve 24VDC leakage approx. 0,02% of kv 90°, PN 10, incl. Position switch 24VDC open/close, 2-wire,50°C, |  | 350 | Bloom | 1 x pneumatic actuator, 1 x 3/2-way solenoid valve | 1 x pneumatic actuator, 1 x 3/2-way solenoid valve
| 1101 |  | 1 | Flexible DN350, length : XXX mm connection one side fixed flange one side loose flange with DVGW, BY OTHERS |  | 350 | Insertec
Compressed air ( 550 l/H, P = 5,5- 10 bar)
Schwietzke | 990 | P-15000-00020-0077 | 1 | Ball valve 3/4" for manual shut off gas and air threaded connection. | KMG V100.720-1 | G 3/4" | Bloom
Elster Kromschröder | 1000 | P-18000-00000-0011 | 2 | Pressure gauge 0 - 10 bar for gas and air ; male threaded stainless steel ; 100mm skale diameter ; with zero point adjustment | RFM 10RB100 | 1/2" | Bloom | 1 | 1
Elster Kromschröder | 1010 | P-19000-00000-0001 | 2 | Pressure gauge cock 1/2" for gas and air with certificate. Rp thread / female / male pemax. 100 bar | MH15 | R 1/2" | Bloom
Norgren | 1020 | P-44000-00000-0005 | 1 | filter/pressure regulator pressure set range 0,4 bis 8 bar Filter bronze 40µm | B68G-6GK-AR3-RLN | G 3/4" | Bloom | 1 | 1
Honeywell | 1040 | P-08000-00000-0043 | 1 | Pressure switch adjustable range 0,5.....6 bar, switching differential 0,15 bar Max Pressure 16 bar Plug connection IP54 | DCM6 | 1/2" | Bloom | 1 | 2
Schwietzke | 1050 | P-15000-00006-0044 | 6 | Ball valve | KMG V100.706 Type 2 | G 1/4" | Bloom
Burner / Media Case / Accessories
Bloom | 10 +14 + 15 | A-M | 2 | Power: 2,95 MW, Gas: 401 Nm³/h @ 165 mbar at the burner Air: 3835 Nm³/h @ 60 mbar Cooling Air: 150 Nm³/h @ ~2 mbar | Burner: M1150-075 | Gas DN80 Prim.Air:DN150 | Bloom |  | 2 x gas nozzle, 2 x baffle
Bloom |  |  | 2 | Construction for mounting above burner Quick change execution | Media case: M1150-0100 |  | Bloom
Bloom | 16 | K-09800-00019-0008 | 2 | Media balls, 2 x 950kg = 1900kg | Media balls |  | Bloom |  | 1900 kg
Bloom | 13 |  | 2 | connection beteen burner and meda case for mounting between burner and media case. | Connection pipe |  | Bloom
Bloom | 20 |  | 2 | Pilot Burner:Capacity: 26 kW, Air: 26 Nm³/h @ 20 mbar, Gas: 2,6 Nm³/h @ 20 mbar | M3001-6101 | Gas R 1/2" Air R 1" | Bloom | 1 | 4 x ignition electrode
Elster Kromschröder | 26 | P-15000-00015-0064 | 2 | ball valve for condensate for manual operation in gas, air , water and oil Rp thread ; pe max 16 bar enviromental temp. -20°C to +60°C EG approval and certificate | AKT 15R160M | R 1/2" | Bloom
Bloom | 5 |  | 2 | Air Cannon for media cases patented worldwide |  |  | Bloom
Siemens | 30 |  | 2 | SITRANS P320 Pressure transmitter Differential pressure and flow PN160 HART (4...20 mA) Measuring cell filling: Silicone oil Maximum measuring span: 250 mbar (24.11 inH²O) Oval flange, fastening thread: M10 (PN160), M12 (PN420) Diaphragm: Stainless steel 316L/1.4404, measuring cell: Stainless steel 316L/1.4404; Sensor Differential pressure no Ex 2 x M20 x 1.5 With display (lid with glass window) Functional Safety (IEC 61508) - SIL2/3; Electrical equipment for furnaces and ancillary equipment (EN 50156-2) General approval without Ex approval: World (CE, RCM) except: EAC, FM, CSA, KCC | 7MF0340-1GM01-5AF2-Z E00 |  | Bloom
Schneider | 31 | P-01050-00015-0001 | 2 | 3 valve manifold NPT for direct connection to transmitter. Connections: Inlet: 1/2" NPT female Outlet: DIN EN 61518; Type A | N542.39.481.01 | 1/2" NPT | Bloom
Elster Kromschröder | 110 + 120 | P-03000-00480-0055 | 2 | BCU480 for pilot and main burner unlimited capacity 1st safety time on start-up: 5 s 2nd safety time on start-up: 3 s safety time during operation: 1 s Air control valve Main voltage: 230 V Ignition transformer: TZI 7,5-12/100 Front film in English Number of start-ups: 2 with Busmodule BCM400SOB2/3-0 Standard communication, Profinet, | BCU480W3P6C0D1000K1E1-/LM400WF3O0E1 |  | Bloom | 2 | 2
| 332 |  | 1 | Zone overtemperature thermocouple, BY OTHERS |  |  | Insertec
| 333 |  | 1 | Zone temperature thermocouple, BY OTHERS |  |  | Insertec
| 334 |  | 1 | Furnace/Bath thermocouple, BY OTHERS |  |  | Insertec
| 335 |  | 1 | SITRANS P320 Pressure transmitter Differential pressure and flow PN160 HART (4...20 mA) Measuring cell filling: Silicone oil Maximum measuring span: 20 mbar (24.11 inH²O) Oval flange, fastening thread: M10 (PN160), M12 (PN420) Diaphragm: Stainless steel 316L/1.4404, measuring cell: Stainless steel 316L/1.4404; Sensor Differential pressure no Ex 2 x M20 x 1.5 With display (lid with glass window) Functional Safety (IEC 61508) - SIL2/3; Electrical equipment for furnaces and ancillary equipment (EN 50156-2) General approval without Ex approval: World (CE, RCM) except: EAC, FM, CSA, KCC | Sitrans P320 7MF0340-1BM01-5AF2-Z E00 |  | Bloom
Schneider | 336 | P-01050-00015-0001 | 1 | 3 valve manifold NPT for direct connection to transmitter. Connections: Inlet: 1/2" NPT female Outlet: DIN EN 61518; Type A | N542.39.481.01 | 1/2" NPT | Bloom
Jasta | 1370 - 1390 |  | 1 | Control butterfly valve for installation between 2 flanges DN 80 PN 10 for air and gas JASTA GD6,100°C. complete assembled with pneumatic actuator, open/close in 3 - 5 seconds max., and Siemens SIPART PS 2, Type: 6DR5010-0NG01-0AA0-Z C20, 4-20 mA in- and output, 24VDC |  | 80 | Bloom | 1 x pneumatic actuator, 1 x Sipart PS 2 | 1 x pneumatic actuator, 1 x Sipart PS 2
Bloom | 1671 |  | 1 | Oxygen delaq system w/ probes, incl. per delaq: (1601-1684) One (1) Pre-piped/cleaned oxygen skid consisting of: safety train, flow metering and flow control valve, for up to 1000 Nm3/h. One (2) oxygen injectors with ancillaries. Two (2) Oxygen probes with necessary cables Oxygen analyzers |  | 80 | Bloom