## ŠP42
|  | Project / Customer: | Construction No. 7502 - Emergency depressurization of UGS Tvrdonice technology, RWE Gas Storage, s.r.o., Prosecká 855/68, 190 00 Prague 9
|  | Document title: | [5 empty] | Job No.: | AE059900
|  | Specification of pneumatic actuators for existing valves | [5 empty] | Document No.:
0599-PS-1000-002
|  | Object: | PS 1000 - Emergency depressurization of CA
|  | Part: | D.2.4 Operating pipeline
Opinion of the bidder regarding individual items pursuant to Section 1.1 of the Request
Basic Information
ITEM | NAME |  | SPECIFICATION
1 | SITE |  | UGS Tvrdonice
2 | VALVE TYPE |  | Existing ball valve with new pneumatic actuator
3 | NOMINAL DIAMETER (DN) |  | 300
4 | NOMINAL PRESSURE (PN) |  | 63
5 | NUMBER |  | 1 pc
6 | DESIGN DESIGNATION |  | ŠP42
7 | MEDIUM |  | Natural gas pursuant to ČSN EN ISO 13 443
8 | MEDIUM TEMPERATURE |  | Operating temperature +5°C through to +15°C Out of operation: -20°C through to +50°C (pipeline at operating pressure, the medium is not flowing)
9 | AMBIENT TEMPERATURE |  | -20 to +50°C
10 | ENVIRONMENT |  | Zone 2 IIA T1 pursuant to ČSN EN 600 79-10-1
11 | OPERATING PRESSURE |  | 2.2 to 6.1 MPa
12 | TEST PRESSURE |  | max. 1.5 multiple of maximum operating pressure (pipeline pressure test before commissioning)
13 | DESIGN |  | SIL design is not required.
14 | EXISTING VALVE DESCRIPTION |  | "Isolating valve with a secure position FO (FO = File Open) for separation equipment and piping underground gas storage (UGS) during emergency conditions. Manufacturer: MSA Type: K83.3.113.214-048 Serial number: B112V16 / 1 Date of manufacture: 11/2011 "
15 | EXISTING ACTUATOR DESCRIPTION |  | MD 15620 (Auma, gearbox GS 125.3-F25-Y, servo-actuator SAEx 1.10)
16 | LOCATION |  | Outdoor, above-ground, on horizontal pipeline (horizontal valve, actuator above the valve). Longitudinal axis of actuator's cylinders will be co-axial with the axis of the longitudinal pipeline in which BV will be installed)
17 | OPERATION TYPE |  | Interrupted operation, common operating mode of seasonal underground gas storage. Envisaged frequency of valve switching below 100 cycles per year.
18 | ACTUATOR SERVICE LIFE |  | at least 30 years in operating conditions specified in this technical specification
DESIGN AND EQUIPMENT OF ACTUATOR
19 | TYPE |  | Pneumatic, single-acting
20 | ACTUATOR OUTPUT |  | The actuator shall be designed for reliable BV opening at DP (Differential Pressure) = 2.0 MPa.
21 | INSTRUMENT AIR |  | Treated instrument air with the pressure between 4.5 bar(g) and 10.0 bar(g) will be available. Reliable function of the actuator at the instrument air pressure of 4.5 bar(g) is required.
22 | INSTRUMENT AIR REGULATION |  | Included in the actuator's scope of supply shall also be the instrument air regulating station including blow-down and filtering of mechanical impurities (so called filter-regulator).
23 | INSTRUMENT AIR CONNECTION |  | The actuator shall be prepared for instrument air connection using 1/4" NPTF
24 | SAFE POSITION |  | In the event of any power supply failure (control voltage, instrument air pressure loss), the actuator shall reliably place BV in "OPEN" safe position (safe position FO - Fail Open), spring opening.
25 | BV OPENING TIME |  | In normal operation, the actuator shall ensure reliable BV closing within 60 seconds.
26 | BV EMERGENCY CLOSING TIME |  | The actuator shall ensure reliable BV closing within 10 seconds whenever the operating state is evaluated as fault or in case of energy loss (control voltage loss, instrument air pressure loss)
27 | HI-PILOT |  | no
28 | ACTUATOR POSITION SENSING |  | The actuator shall be equipped with proximity switches (open/closed), EExi - Namur design (proximity switches equipped with terminal bar for cable connection integrated into the position sensor).
29 | ACTUATOR POSITION INDICATOR |  | The actuator shall be equipped with continuous mechanical position indicator, the end positions "OPEN" and "CLOSED" shall be visibly marked on the actuator (green/red).
30 | ACTUATOR DESIGN |  | The actuator DOES NOT have to be designed as Fire Safe
31 | VALVE CONTROL AND DIAGNOSTICS |  | Valve shall be supplied without manual auxiliary control BV will be equipped with a solenoid valve EExd (or EExe), voltage level 24 VDC - coil with low power consumption <5W. The solenoid valve is used to override BV to a safe position. Solenoid exhaust ports provide a sieve against contamination.
32 | VALVE COMMISSIONING |  | Valve activation in the UGS area shall be performed by supplier's technician after its installation into the pipeline. Valve commissioning shall be performed by the supplier who shall subsequently ensure operator's personnel training in operation and maintenance (both the commissioning and personnel training will be included in the price).
33 | PAINT SYSTEM |  | Paint system and color of the actuator according to the actuator manufacturer's standard; minimum guaranteed service life of the paint system of 15 years
34 | PACKAGING AND PRESERVATION |  | Packaging and preservation of the subject of the supply within the scope of this technical specification shall be performed by the supplier in a way that will protect the supply from mechanical damage during transport and handling at the construction site performed in accordance with the manufacturer's instructions. Parts that could be damaged by corrosion shall be treated with a non-aggressive anti-corrosion product so that the protection against weather effects during storage in the outdoor environment is effective for at least 4 months. Each packaging within the scope of supply shall be designated with identification code specifying individual parts of the supply in the delivery note
35 | STANDARDS AND REGULATIONS |  | TPG 201 01, TPG 935 01, TPG 702 04
36 | QUALITY AND CERTIFICATION |  | EN 10204-3.1 Non-explosiveness certificate must be issued by an authorized test facility accepted in the Czech Republic The product shall bear the CE mark Declaration of conformity shall be issued for the complete actuator and accessories that form part of the actuator pursuant to the provisions of Act No. 22/1997 Coll., as amended.
Scope of Supply
37 |  |  | Existing shut-off BV with installed actuator and all fitted accessories (complete tubing, wiring, ...) according to this technical specification, perfectly adjusted for safe and reliable operation with the parameters specified in this TS.
38 |  |  | All cable grommets (EExe and EExi design depending on the application for cable diameter of 6.2 mm)
39 |  |  | Accompanying technical documentation in Czech language. Installation, operating, and maintenance manual in Czech language.
40 |  |  | Installation, operating, and maintenance manual in Czech language.
41 |  |  | All attestations, certificates, reports on all tests for verification of supply characteristics specified in this technical specification and/or required by applicable generally binding Czech national and European standards and regulations (for example certificate for Fire Safe design, antistatic design, ATEX, ...). Certificate of supply quality and completeness. Declaration of conformity pursuant to the provisions of Act No. 22/1997 Coll., as amended.
All attestations, certificates, and reports shall be delivered by the supplier in Czech or English or German language. Drawings shall be supplied in Czech language. Declaration about warranty and after-warranty service assurance for the actuator in the Czech Republic
42 |  |  | Paint for possible BV and actuator coating repair
43 |  |  | Set of parts for actuator installation and commissioning.
44 |  |  | Technical specification of main components for the purpose of ordering (supply) in case of fault (for example the control air solenoid valve, etc.)
45 |  |  | not applicable
46 |  |  | Set of spare parts for 2 years of operation.
Revision |  | 0 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 4
Date |  | 09/2014 | 04/2015
Proposed by |  | M. Reichl | M. Reichl
Reviewed by |  | J. Pospíšil | J. Pospíšil
Approved by |  | J. Turaz | J. Turaz

## ŠP 15B
|  | Project / Customer: | Construction No. 7502 - Emergency depressurization of UGS Tvrdonice technology, RWE Gas Storage, s.r.o., Prosecká 855/68, 190 00 Prague 9
|  | Document title: | [5 empty] | Job No.: | AE059900
|  | Specification of pneumatic actuators for existing valves | [5 empty] | Document No.:
0599-PS-1000-002
|  | Object: | PS 1000 - Emergency depressurization of CA
|  | Part: | D.2.4 Operating pipeline
Opinion of the bidder regarding individual items pursuant to Section 1.1 of the Request
Basic Information
ITEM | NAME |  | SPECIFICATION
1 | SITE |  | UGS Tvrdonice
2 | VALVE TYPE |  | Existing ball valve with new pneumatic actuator
3 | NOMINAL DIAMETER (DN) |  | 200
4 | NOMINAL PRESSURE (PN) |  | 160
5 | NUMBER |  | 1 pc
6 | DESIGN DESIGNATION |  | ŠP15B
7 | MEDIUM |  | Natural gas pursuant to ČSN EN ISO 13 443
8 | MEDIUM TEMPERATURE |  | Operating temperature +5°C through to +35°C Out of operation: -20°C through to +50°C (pipeline at operating pressure, the medium is not flowing)
9 | AMBIENT TEMPERATURE |  | -20 to +50°C
10 | ENVIRONMENT |  | Zone 2 IIA T1 pursuant to ČSN EN 600 79-10-1
11 | OPERATING PRESSURE |  | 4.5 to 14.1 MPa
12 | TEST PRESSURE |  | max. 1.5 multiple of maximum operating pressure (pipeline pressure test before commissioning)
13 | DESIGN |  | SIL design is not required.
14 | EXISTING VALVE DESCRIPTION |  | Isolating valve with a secure position FO (FO = File Open) for separation equipment and piping underground gas storage (UGS) during emergency conditions. Manufacturer: Armatury Group Type: K91.2 134 Serial number: 111-73610/6
15 | EXISTING ACTUATOR DESCRIPTION |  | Auma, gearbox GS 200.3, servo-actuator SAEx 10.1-F10
16 | LOCATION |  | Outdoor, above-ground, on horizontal pipeline (horizontal valve, actuator above the valve). Longitudinal axis of actuator's cylinders will be co-axial with the axis of the longitudinal pipeline in which BV will be installed)
17 | OPERATION TYPE |  | Interrupted operation, common operating mode of seasonal underground gas storage. Envisaged frequency of valve switching below 100 cycles per year.
18 | ACTUATOR SERVICE LIFE |  | at least 30 years in operating conditions specified in this technical specification
DESIGN AND EQUIPMENT OF ACTUATOR
19 | TYPE |  | Pneumatic, single-acting
20 | ACTUATOR OUTPUT |  | The actuator shall be designed for reliable BV opening at DP (Differential Pressure) = 6,4 MPa.
21 | INSTRUMENT AIR |  | Treated instrument air with the pressure between 4.5 bar(g) and 10.0 bar(g) will be available. Reliable function of the actuator at the instrument air pressure of 4.5 bar(g) is required.
22 | INSTRUMENT AIR REGULATION |  | Included in the actuator's scope of supply shall also be the instrument air regulating station including blow-down and filtering of mechanical impurities (so called filter-regulator).
23 | INSTRUMENT AIR CONNECTION |  | The actuator shall be prepared for instrument air connection using 1/4" NPTF
24 | SAFE POSITION |  | In the event of any power supply failure (control voltage, instrument air pressure loss), the actuator shall reliably place BV in "OPEN" safe position (safe position FO - Fail Open), spring opening.
25 | BV OPENING TIME |  | In normal operation, the actuator shall ensure reliable BV closing within 60 seconds.
26 | BV EMERGENCY CLOSING TIME |  | The actuator shall ensure reliable BV closing within 10 seconds whenever the operating state is evaluated as fault or in case of energy loss (control voltage loss, instrument air pressure loss)
27 | HI-PILOT |  | no
28 | ACTUATOR POSITION SENSING |  | The actuator shall be equipped with proximity switches (open/closed), EExi - Namur design (proximity switches equipped with terminal bar for cable connection integrated into the position sensor).
29 | ACTUATOR POSITION INDICATOR |  | The actuator shall be equipped with continuous mechanical position indicator, the end positions "OPEN" and "CLOSED" shall be visibly marked on the actuator (green/red).
30 | ACTUATOR DESIGN |  | The actuator DOES NOT have to be designed as Fire Safe
31 | VALVE CONTROL AND DIAGNOSTICS |  | Valve shall be supplied without manual auxiliary control BV will be equipped with a solenoid valve EExd (or EExe), voltage level 24 VDC - coil with low power consumption <5W. The solenoid valve is used to override BV to a safe position. Solenoid exhaust ports provide a sieve against contamination.
32 | VALVE COMMISSIONING |  | Valve activation in the UGS area shall be performed by supplier's technician after its installation into the pipeline. Valve commissioning shall be performed by the supplier who shall subsequently ensure operator's personnel training in operation and maintenance (both the commissioning and personnel training will be included in the price).
33 | PAINT SYSTEM |  | Paint system and color of the actuator according to the actuator manufacturer's standard; minimum guaranteed service life of the paint system of 15 years
34 | PACKAGING AND PRESERVATION |  | Packaging and preservation of the subject of the supply within the scope of this technical specification shall be performed by the supplier in a way that will protect the supply from mechanical damage during transport and handling at the construction site performed in accordance with the manufacturer's instructions. Parts that could be damaged by corrosion shall be treated with a non-aggressive anti-corrosion product so that the protection against weather effects during storage in the outdoor environment is effective for at least 4 months. Each packaging within the scope of supply shall be designated with identification code specifying individual parts of the supply in the delivery note
35 | STANDARDS AND REGULATIONS |  | TPG 201 01, TPG 935 01, TPG 702 04
36 | QUALITY AND CERTIFICATION |  | EN 10204-3.1 Non-explosiveness certificate must be issued by an authorized test facility accepted in the Czech Republic The product shall bear the CE mark Declaration of conformity shall be issued for the complete actuator and accessories that form part of the actuator pursuant to the provisions of Act No. 22/1997 Coll., as amended.
Scope of Supply
37 |  |  | Existing shut-off BV with installed actuator and all fitted accessories (complete tubing, wiring, ...) according to this technical specification, perfectly adjusted for safe and reliable operation with the parameters specified in this TS.
38 |  |  | All cable grommets (EExe and EExi design depending on the application for cable diameter of 6.2 mm)
39 |  |  | Accompanying technical documentation in Czech language. Installation, operating, and maintenance manual in Czech language.
40 |  |  | Installation, operating, and maintenance manual in Czech language.
41 |  |  | All attestations, certificates, reports on all tests for verification of supply characteristics specified in this technical specification and/or required by applicable generally binding Czech national and European standards and regulations (for example certificate for Fire Safe design, antistatic design, ATEX, ...). Certificate of supply quality and completeness. Declaration of conformity pursuant to the provisions of Act No. 22/1997 Coll., as amended.
All attestations, certificates, and reports shall be delivered by the supplier in Czech or English or German language. Drawings shall be supplied in Czech language. Declaration about warranty and after-warranty service assurance for the actuator in the Czech Republic
42 |  |  | Paint for possible BV and actuator coating repair
43 |  |  | Set of parts for actuator installation and commissioning.
44 |  |  | Technical specification of main components for the purpose of ordering (supply) in case of fault (for example the control air solenoid valve, etc.)
45 |  |  | not applicable
46 |  |  | Set of spare parts for 2 years of operation.
Revision |  | 0 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 4
Date |  | 09/2014 | 04/2015
Proposed by |  | M. Reichl | M. Reichl
Reviewed by |  | J. Pospíšil | J. Pospíšil
Approved by |  | J. Turaz | J. Turaz

## ŠP16B
|  | Project / Customer: | Construction No. 7502 - Emergency depressurization of UGS Tvrdonice technology, RWE Gas Storage, s.r.o., Prosecká 855/68, 190 00 Prague 9
|  | Document title: | [5 empty] | Job No.: | AE059900
|  | Specification of pneumatic actuators for existing valves | [5 empty] | Document No.:
0599-PS-1000-002
|  | Object: | PS 1000 - Emergency depressurization of CA
|  | Part: | D.2.4 Operating pipeline
Opinion of the bidder regarding individual items pursuant to Section 1.1 of the Request
Basic Information
ITEM | NAME |  | SPECIFICATION
1 | SITE |  | UGS Tvrdonice
2 | VALVE TYPE |  | Existing ball valve with new pneumatic actuator
3 | NOMINAL DIAMETER (DN) |  | 200
4 | NOMINAL PRESSURE (PN) |  | 160
5 | NUMBER |  | 1 pc
6 | DESIGN DESIGNATION |  | ŠP16B
7 | MEDIUM |  | Natural gas pursuant to ČSN EN ISO 13 443
8 | MEDIUM TEMPERATURE |  | Operating temperature +5°C through to +35°C Out of operation: -30°C through to +50°C (pipeline at operating pressure, the medium is not flowing)
9 | AMBIENT TEMPERATURE |  | -20 to +50°C
10 | ENVIRONMENT |  | Zone 2 IIA T1 pursuant to ČSN EN 600 79-10-1
11 | OPERATING PRESSURE |  | 4.5 to 14.1 MPa
12 | TEST PRESSURE |  | max. 1.5 multiple of maximum operating pressure (pipeline pressure test before commissioning)
13 | DESIGN |  | SIL design is not required.
14 | EXISTING VALVE DESCRIPTION |  | Isolating valve with a secure position FO (FO = File Open) for separation equipment and piping underground gas storage (UGS) during emergency conditions. Manufacturer: Armatury Group Type: K91.2 134 Serial number: 111-73610/5
15 | EXISTING ACTUATOR DESCRIPTION |  | Auma, gearbox GS 200.3, servo-actuator SAEx 10.1-F10
16 | LOCATION |  | Outdoor, above-ground, on horizontal pipeline (horizontal valve, actuator above the valve). Longitudinal axis of actuator's cylinders will be co-axial with the axis of the longitudinal pipeline in which BV will be installed)
17 | OPERATION TYPE |  | Interrupted operation, common operating mode of seasonal underground gas storage. Envisaged frequency of valve switching below 100 cycles per year.
18 | ACTUATOR SERVICE LIFE |  | at least 30 years in operating conditions specified in this technical specification
DESIGN AND EQUIPMENT OF ACTUATOR
19 | TYPE |  | Pneumatic, single-acting
20 | ACTUATOR OUTPUT |  | The actuator shall be designed for reliable BV opening at DP (Differential Pressure) = 6,4 MPa.
21 | INSTRUMENT AIR |  | Treated instrument air with the pressure between 4.5 bar(g) and 10.0 bar(g) will be available. Reliable function of the actuator at the instrument air pressure of 4.5 bar(g) is required.
22 | INSTRUMENT AIR REGULATION |  | Included in the actuator's scope of supply shall also be the instrument air regulating station including blow-down and filtering of mechanical impurities (so called filter-regulator).
23 | INSTRUMENT AIR CONNECTION |  | The actuator shall be prepared for instrument air connection using 1/4" NPTF
24 | SAFE POSITION |  | In the event of any power supply failure (control voltage, instrument air pressure loss), the actuator shall reliably place BV in "OPEN" safe position (safe position FO - Fail Open), spring opening.
25 | BV OPENING TIME |  | In normal operation, the actuator shall ensure reliable BV closing within 60 seconds.
26 | BV EMERGENCY CLOSING TIME |  | The actuator shall ensure reliable BV closing within 10 seconds whenever the operating state is evaluated as fault or in case of energy loss (control voltage loss, instrument air pressure loss)
27 | HI-PILOT |  | no
28 | ACTUATOR POSITION SENSING |  | The actuator shall be equipped with proximity switches (open/closed), EExi - Namur design (proximity switches equipped with terminal bar for cable connection integrated into the position sensor).
29 | ACTUATOR POSITION INDICATOR |  | The actuator shall be equipped with continuous mechanical position indicator, the end positions "OPEN" and "CLOSED" shall be visibly marked on the actuator (green/red).
30 | ACTUATOR DESIGN |  | The actuator DOES NOT have to be designed as Fire Safe
31 | VALVE CONTROL AND DIAGNOSTICS |  | Valve shall be supplied without manual auxiliary control BV will be equipped with a solenoid valve EExd (or EExe), voltage level 24 VDC - coil with low power consumption <5W. The solenoid valve is used to override BV to a safe position. Solenoid exhaust ports provide a sieve against contamination.
32 | VALVE COMMISSIONING |  | Valve activation in the UGS area shall be performed by supplier's technician after its installation into the pipeline. Valve commissioning shall be performed by the supplier who shall subsequently ensure operator's personnel training in operation and maintenance (both the commissioning and personnel training will be included in the price).
33 | PAINT SYSTEM |  | Paint system and color of the actuator according to the actuator manufacturer's standard; minimum guaranteed service life of the paint system of 15 years
34 | PACKAGING AND PRESERVATION |  | Packaging and preservation of the subject of the supply within the scope of this technical specification shall be performed by the supplier in a way that will protect the supply from mechanical damage during transport and handling at the construction site performed in accordance with the manufacturer's instructions. Parts that could be damaged by corrosion shall be treated with a non-aggressive anti-corrosion product so that the protection against weather effects during storage in the outdoor environment is effective for at least 4 months. Each packaging within the scope of supply shall be designated with identification code specifying individual parts of the supply in the delivery note
35 | STANDARDS AND REGULATIONS |  | TPG 201 01, TPG 935 01, TPG 702 04
36 | QUALITY AND CERTIFICATION |  | EN 10204-3.1 Non-explosiveness certificate must be issued by an authorized test facility accepted in the Czech Republic The product shall bear the CE mark Declaration of conformity shall be issued for the complete actuator and accessories that form part of the actuator pursuant to the provisions of Act No. 22/1997 Coll., as amended.
Scope of Supply
37 |  |  | Existing shut-off BV with installed actuator and all fitted accessories (complete tubing, wiring, ...) according to this technical specification, perfectly adjusted for safe and reliable operation with the parameters specified in this TS.
38 |  |  | All cable grommets (EExe and EExi design depending on the application for cable diameter of 6.2 mm)
39 |  |  | Accompanying technical documentation in Czech language. Installation, operating, and maintenance manual in Czech language.
40 |  |  | Installation, operating, and maintenance manual in Czech language.
41 |  |  | All attestations, certificates, reports on all tests for verification of supply characteristics specified in this technical specification and/or required by applicable generally binding Czech national and European standards and regulations (for example certificate for Fire Safe design, antistatic design, ATEX, ...). Certificate of supply quality and completeness. Declaration of conformity pursuant to the provisions of Act No. 22/1997 Coll., as amended.
All attestations, certificates, and reports shall be delivered by the supplier in Czech or English or German language. Drawings shall be supplied in Czech language. Declaration about warranty and after-warranty service assurance for the actuator in the Czech Republic
42 |  |  | Paint for possible BV and actuator coating repair
43 |  |  | Set of parts for actuator installation and commissioning.
44 |  |  | Technical specification of main components for the purpose of ordering (supply) in case of fault (for example the control air solenoid valve, etc.)
45 |  |  | not applicable
46 |  |  | Set of spare parts for 2 years of operation.
Revision |  | 0 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 4
Date |  | 09/2014 | 04/2015
Proposed by |  | M. Reichl | M. Reichl
Reviewed by |  | J. Pospíšil | J. Pospíšil
Approved by |  | J. Turaz | J. Turaz