## KK_PN160_FC_ACA
|  | Project / Customer: | Construction No. 7502 - Emergency depressurization of UGS Tvrdonice technology, RWE Gas Storage, s.r.o., Prosecká 855/68, 190 00 Prague 9
|  | Document title: | [5 empty] | Job No.: | AE059900
|  | Specification of shut-off valves PN160 | [5 empty] | Document No.:
0599-PS-1100-001
|  | Object: | PS 1100 - Emergency depressurisation SS North
|  | Part: | D.2.4 Operating pipeline |  |  |  |  | KK PN160 FO ACN DP141
Opinion of the bidder regarding individual items pursuant to Section 1.1 of the Request
Basic information
ITEM | NAME |  | SPECIFICATION
1 | CUSTOMER'S CODE |  | TS-A-14GS002/7201/1/ŠS1
2 | SITE |  | UGS Tvrdonice
3 | VALVE TYPE |  | Ball valve with combined sealing and with pneumatic actuator
4 | NOMINAL DIAMETER (DN) |  | 150
5 | NOMINAL PRESSURE (PN) |  | 160
6 | NUMBER |  | 1 pcs
7 | DESIGN DESIGNATION |  | SŠ1
8 | MEDIUM |  | Natural gas pursuant to ČSN EN ISO 13 443
9 | MEDIUM TEMPERATURE |  | Operating temperature +5°C through to +35°C Out of operation: -20°C through to +50°C (pipeline at operating pressure, the medium is not flowing)
10 | AMBIENT TEMPERATURE |  | -20 to +50°C
11 | ENVIRONMENT |  | Zone 2 IIA T1 pursuant to ČSN EN 600 79-10-1
12 | OPERATING PRESSURE |  | 4.5 to 14.1 MPa
13 | TEST PRESSURE |  | max. 1.5 multiple of maximum operating pressure (pipeline pressure test before commissioning)
14 | DESIGN |  | SIL design is not required.
15 | PURPOSE OF THE VALVE |  | Section shut-off valve with safe position FC (FC = Fail Closed) intended to isolate individual sections of the underground gas storage (UGS) in case of emergencies.
16 | LOCATION |  | Outdoor, above-ground, on horizontal pipeline (horizontal valve, actuator above the valve). Longitudinal axis of actuator's cylinders will be co-axial with the axis of the longitudinal pipeline in which BV will be installed)
17 | OPERATION TYPE |  | Interrupted operation, common operating mode of seasonal underground gas storage. Envisaged frequency of valve switching below 100 cycles per year.
18 | SERVICE LIFE OF BV INCLUDING ACTUATOR |  | at least 30 years in operating conditions specified in this technical specification
Design and equipment of valve
19 | DESIGN |  | Above-ground, with flange, low version without attachments, with single-acting pneumatic actuator, epoxy paint
20 | CONSTRUCTION LENGTH |  | to be determined by supplier - pursuant to ISO 14 313:2007
21 | SAFETY FACTOR |  | 2.15 (for all parts of the BV loaded by pressure) including tubing
22 | TIGHTNESS CLASS |  | Class V pursuant to IEC 60534-4 (valve body must be absolutely impermeable in the direction towards the outside)
23 | BALL SEALING SYSTEM |  | Combined sealing (primary sealing metal-to-metal, secondary soft sealing (exclusively therban)).
24 | EMERGENCY RESEALING OF THE BALL (from DN 200) |  | BV must be equipped with a system for emergency tertiary resealing for the event of BV tightness fault. The resealing preparations (resealing paste, applicator) must be included in the scope of supply.
25 | BV SHAFT |  | Must have the anti-blow-out design preventing its ejection during actuator removal
26 | EMERGENCY RESEALING OF THE SHAFT (from DN 200) |  | BV must be equipped with a system for emergency shaft resealing for the event of sealing failure. The resealing preparations (resealing paste, applicator) must be included in the scope of supply.
27 | SHAFT SEALING |  | BV design shall enable safe replacement of the top shaft sealing during the operation. Control pin will have the "Fire–safe" and "Anti–blow–out" design
28 | CONNECTION TO PIPELINE |  | Flange. Design of flanges pursuant to the provisions of ČSN EN 1092-1 for PN 160, sealing bar B2 (counterflanges, joining material, and seals are not included in the scope of supply).
29 | BV BODY DESIGN |  | Split-body or top-entry. BV body design must enable replacement of the ball and sealing.
30 | BV DESIGN |  | BV must be full-flow, bi-directional, flow reduction may not exceed the values according to the API 6D or EN13942. BV shall have the DBB (double block and bleed) design - from DN 200. BV shall have guaranteed tightness of the intermediate space in both closed and open position. BV shall have the Double Piston Effect (DPE) design (bi-directional, at least one seat must seal in case of the other seat's failure). BV must have the Fire Safe design pursuant to API 6FA. BV must have the antistatic design. BV design must eliminate any cavities where sediments or hydrates impairing its correct function could form. BV must have the TRUNNION design (with supported ball).
31 | CHARPY TEST |  | Shall be carried out pursuant to ISO 14313:2007
32 | BV BLOW-DOWN |  | BV shall be equipped with blow-down - the blow-down will be terminated with a ball valve and closed with pressure plug. Ball valves for BV blow-down must be characterized by long service life. Up to DN 80 (inclusive) - blow-down termination with pressure seal without BV.
33 | BV DEAERATION |  | BV shall be equipped with deaeration of the sealed central part of the body - the deaeration will be terminated with a ball valve and closed with pressure plug. Ball valves for BV deaeration must be characterized by long service life. Up to DN 80 (inclusive) - deaeration termination with pressure seal without BV.
34 | BV POSITION MARKING |  | BV end positions must be visibly and irreplaceably marked on both the valve and the actuator.
35 | BV ACTUATOR CONNECTION |  | Pursuant to ČSN EN ISO 5211
36 | BV INSTALLATION |  | BV body shall be provided with a support for safe, easy, firm, and reliable valve mounting to foundation. BV shall be supplied from the workshop fully assembled, with the actuator and all elements (including tubing, wiring, ...) within the scope pursuant to this specification. The BV+actuator assembly must be equipped with sling points for easy and safe handling using a crane. The sling points shall be located so that any damage to any part of the BV+actuator assembly and/or any damage to its anti-corrosion protection (including paint) is avoided provided that the manufacturer's instructions are observed
37 | MARKING |  | Pursuant to EN 13942, table 12, any and all physical quantities will be indicated in SI units. The label will further specify the customer's CODE (Section 1 of this technical specification).
DESIGN AND EQUIPMENT OF ACTUATOR
38 | TYPE |  | Pneumatic, single-acting
39 | ACTUATOR OUTPUT |  | The actuator shall be designed for reliable BV opening at DP (Differential Pressure) = 2.0 MPa.
40 | INSTRUMENT AIR |  | Treated instrument air with the pressure between 4.5 bar(g) and 10.0 bar(g) will be available. Reliable function of the actuator at the instrument air pressure of 4.5 bar(g) is required.
41 | INSTRUMENT AIR REGULATION |  | Included in the actuator's scope of supply shall also be the instrument air regulating station including blow-down and filtering of mechanical impurities (so called filter-regulator).
42 | INSTRUMENT AIR CONNECTION |  | The actuator shall be prepared for instrument air connection using 1/4" NPTF
43 | SAFE POSITION |  | In the event of any power supply failure (control voltage, instrument air pressure loss), the actuator shall reliably place BV in "CLOSED" safe position (safe position FC - Fail Closed), spring closing.
44 | BV OPENING TIME |  | In normal operation, the actuator shall ensure reliable BV opening within 60 seconds.
45 | BV EMERGENCY CLOSING TIME |  | The actuator shall ensure reliable BV closing within 10 seconds whenever the operating state is evaluated as fault or in case of energy loss (control voltage loss, instrument air pressure loss)
46 | HI-PILOT |  | no
47 | ACTUATOR POSITION SENSING |  | The actuator shall be equipped with proximity switches (open/closed), EExi - Namur design (proximity switches equipped with terminal bar for cable connection integrated into the position sensor).
48 | ACTUATOR POSITION INDICATOR |  | The actuator shall be equipped with continuous mechanical position indicator, the end positions "OPEN" and "CLOSED" shall be visibly marked on the actuator (green/red).
49 | ACTUATOR DESIGN |  | The actuator DOES NOT have to be designed as Fire Safe
50 | VALVE CONTROL AND DIAGNOSTICS |  | Valve shall be supplied without manual auxiliary control The BV+actuator assembly shall be equipped with an automatic valve functionality check system (seizing, sticking, control) – check using the partial lift method (may not cause reduction of BV's internal sectional area). BV shall be equipped with DVC SIS positioner with 4-20mA EExi signal, HART communication protocol, driver for EMERSON AMS system. The valve will be controlled using analog signal 4-20mA where 4mA = valve closed and 20mA = valve open. Positioner's exhaust openings shall be provided with a screen to prevent entry of impurities.
51 | ACTUATOR INSTALLATION ON BV BODY |  | The actuator shall be installed onto the valve and adjusted already in the manufacturing plant - we require supply of complete assembly. Valve activation in the UGS area shall be performed by supplier's technician after its installation into the pipeline. Valve commissioning shall be performed by th supplier who shall subsequently ensure operator's personnel training in operation and maintenance (both the commissioning and personnel training will be included in the price).
52 | PAINT SYSTEM |  | Paint system and color of the BV and actuator according to the BV & actuator manufacturer's standard; minimum guaranteed service life of the paint system of 15 years
53 | PACKAGING AND PRESERVATION |  | Packaging and preservation of the subject of the supply within the scope of this technical specification shall be performed by the supplier in a way that will protect the supply from mechanical damage during transport and handling at the construction site performed in accordance with the manufacturer's instructions. Parts that could be damaged by corrosion shall be treated with a non-aggressive anti-corrosion product so that the protection against weather effects during storage in the outdoor environment is effective for at least 4 months. Internal space of the BV and flange as well as the sealing surfaces of flanges shall be protected by sufficiently strong protective boards and covers. Each packaging within the scope of supply shall be designated with identification code specifying individual parts of the supply in the delivery note
54 | STANDARDS AND REGULATIONS |  | TPG 201 01, TPG 935 01, TPG 702 04
55 | QUALITY AND CERTIFICATION |  | EN 10204-3.1 Non-explosiveness certificate must be issued by an authorized test facility accepted in the Czech Republic The product shall bear the CE mark Declaration of conformity shall be issued for the complete BV including the actuator and accessories that form part of the BV and actuator pursuant to the provisions of Act No. 22/1997 Coll., as amended.
Scope of Supply
56 |  |  | Complete shut-off BV with installed actuator and all fitted accessories (complete tubing, wiring, ...) according to this technical specification, perfectly adjusted for safe and reliable operation with the parameters specified in this TS.
57 |  |  | All cable grommets (EExe and EExi design depending on the application for cable diameter of 6.2 mm)
58 |  |  | Accompanying technical documentation in Czech language. Installation, operating, and maintenance manual in Czech language.
59 |  |  | Installation, operating, and maintenance manual in Czech language.
60 |  |  | All attestations, certificates, reports on all test for verification of supply characteristics specified in this technical specification and/or required by applicable generally binding Czech national and European standards and regulations (for example certificate for Fire Safe design, antistatic design, Charpy test report, ATEX, PED, records on pressure and tightness test of all components in the manufacturing plant, records on non-destructive tests (NDT) of the basic material and welds, ...). Certificate about quality of materials pursuant to the provisions of ČSN EN 10204-3.1 with assigned attestations. Certificate of supply quality and completeness. Declaration of conformity pursuant to the provisions of Act No. 22/1997 Coll., as amended and supplemented.
Product Data Sheet – technical data about the product including drawing of the complete BV+actuator assembly indicating main dimensions, list of parts of the assembly, illustration of details of connection ends, sealing system detail (including emergency resealing), detail of the control shaft sealing system, specification of materials and design of completion, specification of the starting torque (force) for foreseen most demanding operating condition and permitted loading of connecting branches (tension, bending) Separate drawing of the complete BV+actuator assembly indicating the scheme of performed NDT tests All attestations, certificates, and reports shall be supplied in Czech or English or German language. Drawings shall be supplied in Czech language. Declaration about warranty and after-warranty service assurance for both valve and actuator in the Czech Republic
61 |  |  | Paint for possible BV and actuator coating repair
62 |  |  | Set of parts for BV and actuator installation and commissioning.
63 |  |  | Technical specification of main components for the purpose of ordering (supply) in case of fault (for example the blow-down BV, control air solenoid valve, etc.)
64 |  |  | not applicable
65 |  |  | Set of spare parts for 2 years of operation.
Revision |  | 0 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 4
Date |  | 06/2014 | 09/2014 |  | 04/2015
Proposal |  | M. Reichl | M. Reichl |  | M. Reichl
Reviewed by |  | J. Pospíšil | J. Pospíšil |  | J. Pospíšil
Approved by |  | J. Turaz | J. Turaz |  | J. Turaz

## KK_PN160_FO_ACN_DP141
|  | Project / Customer: | Construction No. 7502 - Emergency depressurization of UGS Tvrdonice technology, RWE Gas Storage, s.r.o., Prosecká 855/68, 190 00 Prague 9
|  | Document title: | [5 empty] | Job No.: | AE059900
|  | Specification of shut-off valves PN160 | [5 empty] | Document No.:
0599-PS-1100-001
|  | Object: | PS 1100 - Emergency depressurisation SS North
|  | Part: | D.2.4 Operating pipeline |  |  |  |  | KK PN160 FO ACN DP141
Opinion of the bidder regarding individual items pursuant to Section 1.1 of the Request
Basic information
ITEM | NAME |  | SPECIFICATION
1 | CUSTOMER'S CODE |  | TS-A-14GS002/7201/1/XV001; TS-A-14GS002/7201/1/XV002; TS-A-14GS002/7201/1/XV003; TS-A-14GS002/7201/1/XV004
2 | SITE |  | UGS Tvrdonice
3 | VALVE TYPE |  | Ball valve with metal - metal sealing and with pneumatic actuator
4 | NOMINAL DIAMETER (DN) |  | 50 (XV 001, XV002), 25 (XV003, XV004)
5 | NOMINAL PRESSURE (PN) |  | 160
6 | NUMBER |  | 4 pcs
7 | DESIGN DESIGNATION |  | XV001 XV002 XV003 XV004
8 | MEDIUM |  | Natural gas pursuant to ČSN EN ISO 13 443
9 | MEDIUM TEMPERATURE |  | Operating temperature +5°C through to +35°C Out of operation: -20°C through to +50°C (pipeline at operating pressure, the medium is not flowing)
10 | AMBIENT TEMPERATURE |  | -20 to +50°C
11 | ENVIRONMENT |  | Zone 2 IIA T1 pursuant to ČSN EN 600 79-10-1
12 | OPERATING PRESSURE |  | 4.5 to 14.1 MPa
13 | TEST PRESSURE |  | max. 1.5 multiple of maximum operating pressure (pipeline pressure test before commissioning)
14 | DESIGN |  | SIL design is not required.
15 | PURPOSE OF THE VALVE |  | Section shut-off valve with safe position FO(FO = Fail Open) intended to isolate individual sections of the underground gas storage (UGS) in case of emergencies.
16 | LOCATION |  | Outdoor, above-ground, on horizontal pipeline (horizontal valve, actuator above the valve).Armature XV-001 and XV002 on the vertical pipe, actuator vertically. Longitudinal axis of actuator's cylinders will be co-axial with the axis of the longitudinal pipeline in which BV will be installed)
17 | OPERATION TYPE |  | Interrupted operation, common operating mode of seasonal underground gas storage. Envisaged frequency of valve switching below 100 cycles per year.
18 | SERVICE LIFE OF BV INCLUDING ACTUATOR |  | at least 30 years in operating conditions specified in this technical specification
Design and equipment of valve
19 | DESIGN |  | Above-ground, with flange, low version without attachments, with single-acting pneumatic actuator, epoxy paint
20 | CONSTRUCTION LENGTH |  | to be determined by supplier - pursuant to ISO 14 313:2007
21 | SAFETY FACTOR |  | 2.15 (for all parts of the BV loaded by pressure) including tubing
22 | TIGHTNESS CLASS |  | Class V pursuant to IEC 60534-4 (valve body must be absolutely impermeable in the direction towards the outside)
23 | BALL SEALING SYSTEM |  | Metal-metal sealing
24 | EMERGENCY RESEALING OF THE BALL (from DN 200) |  | BV must be equipped with a system for emergency tertiary resealing for the event of BV tightness fault. The resealing preparations (resealing paste, applicator) must be included in the scope of supply.
25 | BV SHAFT |  | Must have the anti-blow-out design preventing its ejection during actuator removal
26 | EMERGENCY RESEALING OF THE SHAFT (from DN 200) |  | BV must be equipped with a system for emergency shaft resealing for the event of sealing failure. The resealing preparations (resealing paste, applicator) must be included in the scope of supply.
27 | SHAFT SEALING |  | BV design shall enable safe replacement of the top shaft sealing during the operation. Control pin will have the "Fire–safe" and "Anti–blow–out" design
28 | CONNECTION TO PIPELINE |  | Flange. Design of flanges pursuant to the provisions of ČSN EN 1092-1 for PN 160, sealing bar B2 (counterflanges, joining material, and seals are not included in the scope of supply).
29 | BV BODY DESIGN |  | Split-body or top-entry. BV body design must enable replacement of the ball and sealing.
30 | BV DESIGN |  | BV must be full-flow, bi-directional, flow reduction may not exceed the values according to the API 6D or EN13942. BV shall have the DBB (double block and bleed) design - from DN 200. BV shall have guaranteed tightness of the intermediate space in both closed and open position. BV shall have the Double Piston Effect (DPE) design (bi-directional, at least one seat must seal in case of the other seat's failure). BV must have the Fire Safe design pursuant to API 6FA. BV must have the antistatic design. BV design must eliminate any cavities where sediments or hydrates impairing its correct function could form. BV must have the TRUNNION design (with supported ball) - Outside DN 25.
31 | CHARPY TEST |  | Shall be carried out pursuant to ISO 14313:2007
32 | BV BLOW-DOWN |  | BV shall be equipped with blow-down - the blow-down will be terminated with a ball valve and closed with pressure plug. Ball valves for BV blow-down must be characterized by long service life. Up to DN 80 (inclusive) - blow-down termination with pressure seal without BV.
33 | BV DEAERATION |  | BV shall be equipped with deaeration of the sealed central part of the body - the deaeration will be terminated with a ball valve and closed with pressure plug. Ball valves for BV deaeration must be characterized by long service life. Up to DN 80 (inclusive) - deaeration termination with pressure seal without BV.
34 | BV POSITION MARKING |  | BV end positions must be visibly and irreplaceably marked on both the valve and the actuator.
35 | BV ACTUATOR CONNECTION |  | Pursuant to ČSN EN ISO 5211
36 | BV INSTALLATION |  | BV body shall be provided with a support for safe, easy, firm, and reliable valve mounting to foundation. BV shall be supplied from the workshop fully assembled, with the actuator and all elements (including tubing, wiring, ...) within the scope pursuant to this specification. The BV+actuator assembly must be equipped with sling points for easy and safe handling using a crane. The sling points shall be located so that any damage to any part of the BV+actuator assembly and/or any damage to its anti-corrosion protection (including paint) is avoided provided that the manufacturer's instructions are observed
37 | MARKING |  | Pursuant to EN 13942, table 12, any and all physical quantities will be indicated in SI units. The label will further specify the customer's CODE (Section 1 of this technical specification).
DESIGN AND EQUIPMENT OF ACTUATOR
38 | TYPE |  | Pneumatic, single-acting
39 | ACTUATOR OUTPUT |  | The actuator shall be designed for reliable BV opening at DP (Differential Pressure) = 14.1 MPa.
40 | INSTRUMENT AIR |  | Treated instrument air with the pressure between 4.5 bar(g) and 10.0 bar(g) will be available. Reliable function of the actuator at the instrument air pressure of 4.5 bar(g) is required.
41 | INSTRUMENT AIR REGULATION |  | Included in the actuator's scope of supply shall also be the instrument air regulating station including blow-down and filtering of mechanical impurities (so called filter-regulator).
42 | INSTRUMENT AIR CONNECTION |  | The actuator shall be prepared for instrument air connection using 1/4" NPTF
43 | SAFE POSITION |  | In the event of any power supply failure (control voltage, instrument air pressure loss), the actuator shall reliably place BV in "OPEN" safe position (safe position FO - Fail Open), spring opening .
44 | BV OPENING TIME |  | In normal operation, the actuator shall ensure reliable BV closing within 60 seconds.
45 | BV EMERGENCY CLOSING TIME |  | The actuator shall ensure reliable BV opening within 10 seconds whenever the operating state is evaluated as fault or in case of energy loss (control voltage loss, instrument air pressure loss)
46 | HI-PILOT |  | no
47 | ACTUATOR POSITION SENSING |  | The actuator shall be equipped with proximity switches (open/closed), EExi - Namur design (proximity switches equipped with terminal bar for cable connection integrated into the position sensor).
48 | ACTUATOR POSITION INDICATOR |  | The actuator shall be equipped with continuous mechanical position indicator, the end positions "OPEN" and "CLOSED" shall be visibly marked on the actuator (green/red).
49 | ACTUATOR DESIGN |  | The actuator DOES NOT have to be designed as Fire Safe
50 | VALVE CONTROL AND DIAGNOSTICS |  | Valve shall be supplied without manual auxiliary control KK will be equipped with the solenoid valve in the execution EExd (or EExem), tension level 24 VDC-coil with low wattage < 5W. Solenoid valve is used to switch the KK into a safe position. Positioner's exhaust openings shall be provided with a screen to prevent entry of impurities.
51 | ACTUATOR INSTALLATION ON BV BODY |  | The actuator shall be installed onto the valve and adjusted already in the manufacturing plant - we require supply of complete assembly. Valve activation in the UGS area shall be performed by supplier's technician after its installation into the pipeline. Valve commissioning shall be performed by th supplier who shall subsequently ensure operator's personnel training in operation and maintenance (both the commissioning and personnel training will be included in the price).
52 | PAINT SYSTEM |  | Paint system and color of the BV and actuator according to the BV & actuator manufacturer's standard; minimum guaranteed service life of the paint system of 15 years
53 | PACKAGING AND PRESERVATION |  | Packaging and preservation of the subject of the supply within the scope of this technical specification shall be performed by the supplier in a way that will protect the supply from mechanical damage during transport and handling at the construction site performed in accordance with the manufacturer's instructions. Parts that could be damaged by corrosion shall be treated with a non-aggressive anti-corrosion product so that the protection against weather effects during storage in the outdoor environment is effective for at least 4 months. Internal space of the BV and flange as well as the sealing surfaces of flanges shall be protected by sufficiently strong protective boards and covers. Each packaging within the scope of supply shall be designated with identification code specifying individual parts of the supply in the delivery note
54 | STANDARDS AND REGULATIONS |  | TPG 201 01, TPG 935 01, TPG 702 04
55 | QUALITY AND CERTIFICATION |  | EN 10204-3.1 Non-explosiveness certificate must be issued by an authorized test facility accepted in the Czech Republic The product shall bear the CE mark Declaration of conformity shall be issued for the complete BV including the actuator and accessories that form part of the BV and actuator pursuant to the provisions of Act No. 22/1997 Coll., as amended.
Scope of Supply
56 |  |  | Complete shut-off BV with installed actuator and all fitted accessories (complete tubing, wiring, ...) according to this technical specification, perfectly adjusted for safe and reliable operation with the parameters specified in this TS.
57 |  |  | All cable grommets (EExe and EExi design depending on the application for cable diameter of 6.2 mm)
58 |  |  | Accompanying technical documentation in Czech language. Installation, operating, and maintenance manual in Czech language.
59 |  |  | Installation, operating, and maintenance manual in Czech language.
60 |  |  | All attestations, certificates, reports on all test for verification of supply characteristics specified in this technical specification and/or required by applicable generally binding Czech national and European standards and regulations (for example certificate for Fire Safe design, antistatic design, Charpy test report, ATEX, PED, records on pressure and tightness test of all components in the manufacturing plant, records on non-destructive tests (NDT) of the basic material and welds, ...). Certificate about quality of materials pursuant to the provisions of ČSN EN 10204-3.1 with assigned attestations. Certificate of supply quality and completeness. Declaration of conformity pursuant to the provisions of Act No. 22/1997 Coll., as amended and supplemented.
Product Data Sheet – technical data about the product including drawing of the complete BV+actuator assembly indicating main dimensions, list of parts of the assembly, illustration of details of connection ends, sealing system detail (including emergency resealing), detail of the control shaft sealing system, specification of materials and design of completion, specification of the starting torque (force) for foreseen most demanding operating condition and permitted loading of connecting branches (tension, bending) Separate drawing of the complete BV+actuator assembly indicating the scheme of performed NDT tests All attestations, certificates, and reports shall be supplied in Czech or English or German language. Drawings shall be supplied in Czech language. Declaration about warranty and after-warranty service assurance for both valve and actuator in the Czech Republic
61 |  |  | Paint for possible BV and actuator coating repair
62 |  |  | Set of parts for BV and actuator installation and commissioning.
63 |  |  | Technical specification of main components for the purpose of ordering (supply) in case of fault (for example the blow-down BV, control air solenoid valve, etc.)
64 |  |  | not applicable
65 |  |  | Set of spare parts for 2 years of operation.
Revision |  | 0 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 4
Date |  | 06/2014 | 09/2014 |  | 04/2015
Proposal |  | M. Reichl | M. Reichl |  | M. Reichl
Reviewed by |  | J. Pospíšil | J. Pospíšil |  | J. Pospíšil
Approved by |  | J. Turaz | J. Turaz |  | J. Turaz