|  | Sliding Stem Valve Specification |  |
| --- | --- | --- |

| Customer: INTECHA Praha |  |  | Emerson Process Management, s.r.o. |  |
| --- | --- | --- | --- | --- |
| Contact: |  |  | Contact: Martin Lepold |  |
| Customer Reference: Intecha-prepocet-PZP |  |  | Sales Office Reference: | Lead Time: 5 Day(s) |
| Item: 100 | Rev: | Qty: 2 | Quote: 412-VD-161221-0002760 / Intecha-prepocet-PZP | Rev: D |
| Tags: LV 4RT001AA001,LV 4RT002AA001 |  |  | Date Last Modified: 27/01/2017 |  |
| Description: NPS 1 ES European Directives 667 Size 40i DVC6200 Factory Mtgs DVC6200/DVC2000 ATEX Compliance -EU Process Level 3 Global Drawings |  |  |  |  |
| Service Description: |  |  |  |  |

| Service: |  | Positioner Type: | DVC6200,Advanced-AD |
| --- | --- | --- | --- |
| Size and Type: | DN 25 ES | Input Signal: | 4 to 20 mA dc |
| Body Style: | Globe | Access: | 67CFR Filter/Regulator |
| Design Temp: | 20 deg C | Gauges: | 0-160 psig/0-11 bar |
| Design Press: | 4.3 MPa(a) | Action: | Direct |
| End Connect/In/Out: | PN 63/*RF(EN1092-1/21 B)/*RF(EN1092-1/21 B) | Certification: | ATEX EExi |
| Material: | WC9 Alloy Steel | Controller Type: |  |
| Ports: | 1 | Action: |  |
| Flow Direction: | Down | Measure Element: |  |
| Trim Number: | 440C SST | Range: |  |
| Cage Matl: | S17400 SST | Output: |  |
| Retainer Matl: |  | Mounting: |  |
| Bushing Matl: |  | Airset: |  |
| Seat Ring Matl: | S44004 SST | Mounting: |  |
| VALVE PLUG |  | Transducer: |  |
| Material: | S44004 SST | Input Signal: |  |
| Guiding: | Cage | Output Signal: |  |
| Balance: | Unbalanced | Action: |  |
| Shutoff Class: | ANSI CL V | Mounting: |  |
| Port Size: | 1 Inch | Airset: |  |
| Characteristic: | Cav III, 2 Stage, Micro-Flat | Certifications: |  |
| Stem Material: | S31600 SST | Line In: | 2 in, SCH STD |
| Stem Size: | 1/2 Inch | Line Out: | 2 in, SCH STD |
| Bonnet Style: | Plain | Insulation: |  |
| Boss Size: | 2 13/16 | Service Cond: |  |
| Packing: | Single PTFE | Process Fluid: | TEG |
| Access: | No | Critical Pressure: | 22000.000 kPa(a) |
| Bolt, Bonnet: | SA-193-B7 Studs/2H Nuts | Shutoff Drop: | 43.000 bar |
| PackFlg/Bltg: | SST Pkg Flg, SST Studs & Nuts |  |  |
| Actuator: | Spring & Diaphragm |  |  |
| Type/Size: | 667/40i |  |  |
| Travel: | 1 Inch |  |  |
| Bench Set: | 9-30 psi |  |  |
| Push Down To: | PDTC |  |  |
| Supply: | Air |  |  |
| To Actuator: | 0 to 50 psig |  |  |
| Fails Valve: | Close |  |  |
| Handwheel: | None | Max Rated Cv: | 2.3 |

|  | Variable Name | Unit |  | Normal | Maximum |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Mass flow rate Liquid (wl) | kg/h |  | 1500.0000 | 3250.0000 |  |
|  | Inlet Pressure (P1) | MPa(a) |  | 1.100000 | 4.300000 |  |
|  | Pressure Change (dP) | MPa |  | 0.980000 | 4.200000 |  |
|  | Temperature (T1) | deg C |  | 15.0000 | 20.0000 |  |
|  | SG |  |  | 1.110 | 1.110 |  |
|  | Dynamic Viscosity (Mu) | mPa.s |  | 12.300 | 12.300 |  |
|  | Vapor Pressure (Pv) | kPa(a) |  | 6.000 | 6.000 |  |
|  | Sizing Coefficient (Cv) |  |  | 0.526 | 0.562 |  |
|  | % Open |  |  | 46 | 48 |  |
|  | Valve Lpa (LpAe1m) | dB(A) |  | < 50 | 50 |  |

| NOTES: |  |
| --- | --- |

|  | Sliding Stem Valve Specification |  |
| --- | --- | --- |

| Customer: INTECHA Praha |  |  | Emerson Process Management, s.r.o. |  |
| --- | --- | --- | --- | --- |
| Contact: |  |  | Contact: Martin Lepold |  |
| Customer Reference: Intecha-prepocet-PZP |  |  | Sales Office Reference: | Lead Time: 5 Day(s) |
| Item: 210 | Rev: | Qty: 2 | Quote: 412-VD-161221-0002760 / Intecha-prepocet-PZP | Rev: D |
| Tags: TV 4RT001AA002,TV 4RT002AA002 |  |  | Date Last Modified: 27/01/2017 |  |
| Description: DN 25 GX European Directives DVC6200 Factory Mtgs DVC6200/DVC2000 ATEX Compliance -EU Process Level 3 Global Drawings |  |  |  |  |
| Service Description: |  |  |  |  |

| Service: |  | Positioner Type: | DVC6200,Advanced-AD |
| --- | --- | --- | --- |
| Size and Type: | DN 25 GX | Input Signal: | 4 to 20 mA dc |
| Body Style: | Globe | Access: | 67CFR Filter/Regulator |
| Design Temp: | 20 deg C | Gauges: | 0-160 psig/0-11 bar |
| Design Press: | 0.15 MPa(a) | Action: | Direct |
| End Connect/In/Out: | PN 10/16/25/40/RF(EN1092-1/21 B)/RF(EN1092-1/21 B) | Certification: | ATEX EExi |
| Material: | 1.0619 Steel | Controller Type: |  |
| Ports: | 1 | Action: |  |
| Flow Direction: | Up | Measure Element: |  |
| Trim Number: | Standard | Range: |  |
| Cage Matl: | Not App | Output: |  |
| Retainer Matl: |  | Mounting: |  |
| Bushing Matl: |  | Airset: |  |
| Seat Ring Matl: | CF3M SST | Mounting: |  |
| VALVE PLUG |  | Transducer: |  |
| Material: | S31603 SST | Input Signal: |  |
| Guiding: | Stem | Output Signal: |  |
| Balance: | Unbalanced | Action: |  |
| Shutoff Class: | ANSI CL V Air Test | Mounting: |  |
| Port Size: | 22 mm | Airset: |  |
| Characteristic: | Linear | Certifications: |  |
| Stem Material: | S31603 SST | Line In: | 2 in, SCH STD |
| Stem Size: | 10 mm | Line Out: | 2 in, SCH STD |
| Bonnet Style: | Standard | Insulation: |  |
| Boss Size: |  | Service Cond: |  |
| Packing: | Live Loaded PTFE | Process Fluid: | TEG |
| Access: |  | Critical Pressure: | 22000.000 kPa(a) |
| Bolt, Bonnet: | SA-193-B7 Studs/2H Nuts | Shutoff Drop: |  |
| PackFlg/Bltg: |  |  |  |
| Actuator: | Spring & Diaphragm |  |  |
| Type/Size: | GX/225 |  |  |
| Travel: | 20 mm |  |  |
| Bench Set: |  |  |  |
| Push Down To: | PDTC |  |  |
| Supply: | Air |  |  |
| To Actuator: | 4.0 to 6.0 barg (58 to 87 psig) |  |  |
| Fails Valve: | Close (ATO) |  |  |
| Handwheel: | None | Max Rated Cv: | 17.4 |

|  | Variable Name | Unit |  | Normal | Maximum |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Mass flow rate Liquid (wl) | kg/h |  | 200.0000 | 3250.0000 |  |
|  | Inlet Pressure (P1) | MPa(a) |  | 0.110000 | 0.150000 |  |
|  | Pressure Change (dP) | MPa |  | 0.010000 | 0.010000 |  |
|  | Temperature (T1) | deg C |  | 15.0000 | 20.0000 |  |
|  | SG |  |  | 1.110 | 1.110 |  |
|  | Dynamic Viscosity (Mu) | mPa.s |  | 12.300 | 12.300 |  |
|  | Vapor Pressure (Pv) | kPa(a) |  | 6.000 | 6.000 |  |
|  | Sizing Coefficient (Cv) |  |  | 0.695 | 12.076 |  |
|  | % Open |  |  | 9 | 77 |  |
|  | Valve Lpa (LpAe1m) | dB(A) |  | < 50 | < 50 |  |

| NOTES: |  |
| --- | --- |